## 1. Introduction
Welcome to the National Grid's Port Peak Power Demand Calculation Tool
Developed by Siemens Power Technologies International GB&I
Background
Electrical infrastructure will be affected by the electrification of shipping and ports, as well as the shift to onsite production of alternative low-carbon fuels. Understanding potential increases in peak power demand is of primary importance because infrastructure must be sufficiently sized to accommodate it.
Future needs must be considered and planned for now in order for the Transmission Systems Operator and Distribution Systems Operators to plan works effectively.
This tool is designed to make preliminary estimates of peak power demand up to 2040, in 5 year intervals, from a set of simplified user inputs.
It should be considered a simple “peak power calculator” for ports and stakeholders to indicate at a high level the demands which may be coming down the line and potential implications.
Users
Primary users: Ports
Secondary users: Energy network operators, Government, and Regulators.
Design Principles
  Simple tool
  User inputs minimised
  Assumptions and references communicated clearly
  Limitations of output communicated clearly
  High level implications, advice and recommendations made by National Grid
Siemens Disclaimer
Siemens Power Technologies International GB&I
This Tool was produced by Siemens for publication on National Grid Electricity Transmission plc’s (“NGET”) website and use by port owners / operators who access NGET’s website to work out their approximate peak demand for future years (“Stated Purpose”). This Tool is meant to be used as a whole and in conjunction with this disclaimer. Any use of this Tool other than as a whole and in conjunction with this disclaimer is forbidden. Any use of this Tool outside of its Stated Purpose without the prior written consent of Siemens is forbidden. Except for its Stated Purpose, this Tool may not be copied or distributed in whole or in part without Siemens' prior written consent.
This Tool and the information and statements herein are based in whole or in part on information obtained from various sources as of 30/07/2021. While Siemens and NGET believes such information to be accurate, they make no assurances, endorsements or warranties, express or implied, as to the validity, accuracy or completeness of any such information, any conclusions based thereon, or any methods disclosed in this Tool. Siemens and NGET assume no responsibility for the results of any actions and inactions taken on the basis of this Tool. By a party using, acting or relying on this Tool, such party consents and agrees that Siemens and NGET, their employees, directors, officers, contractors, advisors, members, affiliates, successors and agents shall have no liability with respect to such use, actions, inactions, or reliance.
This Tool does contain some forward-looking opinions. Certain unanticipated factors could cause actual results to differ from the opinions contained herein. Forward-looking opinions are based on historical and/or current information that relate to future operations, strategies, financial results or other developments. Some of the technological changes, competitive conditions, new products, general economic conditions, changes in tax laws, adequacy of reserves, credit and other risks associated with Corning and/or other third parties, significant changes in interest rates and fluctuations in foreign currency exchange rates. Further, certain statements, findings and conclusions in this Tool are based on Siemens' interpretations of various contracts. Interpretations of these contracts by legal counsel or a jurisdictional body could differ.
1. Introduction
3. Assumptions
7. Function outputs
8. Outputs
6. Functions
5. Assumed constants
4. User inputs
2. Instructions

## 2. Instructions
Data entry fields are colour coded for guidance:
User input
Referenced assumed constant
Unreferenced assumed constant
Calculation
Output
Nomenclature
GW | Gigawatt
H2 | Hydrogen
HGV | Heavy Goods Vehicles
kW | Kilowatt
Lo Lo | Lift-on/Lift-off
MW | Megawatt
NH3 | Ammonia
RoPax | Roll-on/roll-off passenger
Ro-Ro | Roll-on/roll-off
How to use this tool:
Developed by Siemens Power Technologies International GB&I
The Port Peak Demand Tool is split into eight sections - see excel tabs. The current section is highlighted within the arrow flow diagram at the top of each page. All tabs are viewable by users.
Tabs '1. Introduction', '2. Instructions' and '3. Model assumptions' are for information.
Tabs '4. User inputs' and '5. Assumed constant' are data inputs to the tool functions. Only cells within the '4. User inputs' tab are editable.
Tab '6. Functions' includes the main calculations for the tool.
Tab '7. Function outputs' gives a summary of total function outputs per asset up to 2040.
Tab '8. Outputs' gives the total site peak demand up to 2040 with recommendations from National Grid on next steps.
If you require, a Developer version of the tool - allowing editor rights for all tabs - please contact box.DecarbTransport@nationalgrid.com
User inputs:
When inputting data, an exact match may not be availble, in this case use the closest alternative. For example, if there is a vessel type that regularly uses your port but isn't available as a user input you should use most similar vessel option to input your values.
Of note, for the user input 'Berths' only consider berths and not moorings.
Where multiple vessel types use the same berth - consider that berth type as the largest vessel the berth can hold
For specialist equipment such as self-loaders, conveyors, hoppers, navigational lights, radar and communications equipment, please specify the peak power demand for each asset under optional inputs. Specific specialist equipment has not been listed as they vary between ports.
1. Introduction
3. Assumptions
7. Function outputs
8. Outputs
6. Functions
5. Assumed constants
4. User inputs
2. Instructions

## 3. Assumptions
Modelling Assumptions
Developed by Siemens Power Technologies International GB&I
In the process of developing the tool a number of modelling assumptions were made, these include:
General
  - Wherever possible assumed inputs are taken from reliable reference documents, however when data was not available inputs are assumed based on industry knowledge.
  - Port infrastructure assets and other equipment remain the same up to 2040.
  - Assumed no major upgrades to port, such as additional berths or expansion of any existing berths.
  - Where a range of values is possible, the largest is used to account for peak demand.
  - Building and co-located industries are excluded from the model as their energy demand is negligible.
Vessels
  - Naval, fishing, research and leisure vessels are not included in the model as they make up a relatively small proportion of electrical demand.
  - Current vessel fuel is Marine Diesel.
  - Where no alternative information is available, in future vessel fuels will be hydrogen or ammonia.
  - Vessels will have enough space available for hydrogen based fuels.
  - Vessel charging requirements are matched by port infrastructure.
  - Port traffic remains the same up to 2040.
Vehicles
  - Vehicle chargers are assumed as fast chargers.
  - HGVs will use hydrogen based fuels.
Siemens Disclaimer
Siemens Power Technologies International GB&I
This Tool was produced by Siemens for publication on National Grid Electricity Transmission plc’s (“NGET”) website and use by port owners / operators who access NGET’s website to work out their approximate peak demand for future years (“Stated Purpose”). This Tool is meant to be used as a whole and in conjunction with this disclaimer. Any use of this Tool other than as a whole and in conjunction with this disclaimer is forbidden. Any use of this Tool outside of its Stated Purpose without the prior written consent of Siemens is forbidden. Except for its Stated Purpose, this Tool may not be copied or distributed in whole or in part without Siemens' prior written consent.
This Tool and the information and statements herein are based in whole or in part on information obtained from various sources as of 30/07/2021. While Siemens and NGET believes such information to be accurate, they make no assurances, endorsements or warranties, express or implied, as to the validity, accuracy or completeness of any such information, any conclusions based thereon, or any methods disclosed in this Tool. Siemens and NGET assume no responsibility for the results of any actions and inactions taken on the basis of this Tool. By a party using, acting or relying on this Tool, such party consents and agrees that Siemens and NGET, their employees, directors, officers, contractors, advisors, members, affiliates, successors and agents shall have no liability with respect to such use, actions, inactions, or reliance.
This Tool does contain some forward-looking opinions. Certain unanticipated factors could cause actual results to differ from the opinions contained herein. Forward-looking opinions are based on historical and/or current information that relate to future operations, strategies, financial results or other developments. Some of the technological changes, competitive conditions, new products, general economic conditions, changes in tax laws, adequacy of reserves, credit and other risks associated with Corning and/or other third parties, significant changes in interest rates and fluctuations in foreign currency exchange rates. Further, certain statements, findings and conclusions in this Tool are based on Siemens' interpretations of various contracts. Interpretations of these contracts by legal counsel or a jurisdictional body could differ.
1. Introduction
3. Assumptions
7. Function outputs
8. Outputs
6. Functions
5. Assumed constants
4. User inputs
2. Instructions
Reference documents
Developed by Siemens Power Technologies International GB&I
Reference code Document details
ABS2020 ABS Pathways to sustainable shipping - setting the course to low carbon shipping
BPA2020 British Ports Association - Reducing emissions from shipping in ports: Examining the barriers to shore power
CSB2020 Croatian Ship Building - Ro-Ro cargo vessels
CT2018 Shanghai ReeferCo Container Co. - Technical specification for refrigerated containers
CWind2020 CWind - CWind pioneer - hybrid SES CTV
DAF2021 DAF - Specification sheet XF 450
EFTE2018 Transport and Environment - Roadmap to decarbonising European shipping
EMSA2020 European Maritime Safety Agency - Study on electrical energy storage for ships
EPRI2015 Electric Power Research Institute - Electric forklifts
HijosDJ2021 Hijos De J. Barreras - Refrigerated Cargo Vessels
ICCT2015 The International Council on Clean Transport - Costs and benefits of shore power at the port of Shenzhen
IDEALHY2013 Integrated Design for Efficient Advanced Liquification of Hydrogen - Efficient liquefaction of Hydrogen: Results of the IDEALHY Project
IRENA2018 International Renewable Energy Agency - Hydrogen from Renewable Power
JFMS2021 James Fisher Marine Services - Offshore support vessel
LIEB2020 Liebherr - Technical description rubber tyred gantry crane
LIEBMHC2020 Liebherr - Product range mobile harbour cranes
Renault2013 Renault - Long haul range T
Siemens2020 Siemens - High voltage charging solutions
Siemens2021 Siemens - Sicharge UC - Powerful charging solution for your electric fleet
TE2021 Transport and Environment - Decarbonising European shipping
TEN2020 Transport Energy Network - A collaborative approach to understanding decarbonised transport in 2050
WBCSD2020 wbcsd - Shore-to-ship power
WSDoE1994 Washington State Department of Ecology - Guidelines for Determining Oil Spill Volumes in the Field

## 4. User inputs
Port infrastrucutre |  |  |  | Traffic
N.B. if user inputs are not an exact match use the most similar alternative. N.B. Consider they berth type as the largest vessel the berth can hold. |  |  |  | N.B. if user inputs are not an exact match use the most similar alternative
Berths | Number | Unit | Reference | Vessel traffic | Unit | Reference
Dry Bulk |  | Number |  | Dry Bulk | Number / day
Liquid Bulk |  | Number |  | Liquid Bulk | Number / day
Container Lo-Lo |  | Number |  | Container Lo-Lo | Number / day
Other General Cargo |  | Number |  | Other General Cargo | Number / day
Ro-Ro (vehicle carriers) |  | Number |  | Ro-Ro (vehicle carriers) | Number / day
Ro-Ro (unaccompanied) |  | Number |  | Ro-Ro (unaccompanied) | Number / day
Ferry / RoPAX |  | Number |  | Ferry / RoPAX | Number / day
Cruise |  | Number |  | Cruise | Number / day
Reefers |  | Number |  | Reefers | Number / day
Crew Transfer Vessels |  | Number |  | Crew Transfer Vessels | Number / day
Offshore Support Vessels |  | Number |  | Offshore Support Vessels | Number / day
Pilot boats & harbour craft |  | Number |  | Pilot boats & harbour craft | Number / day
Rigs |  | Number |  | Rigs | Number / day
Vehicles |  | Unit | Reference | Outbound HGV traffic | Unit | Reference
Car parking spaces |  | Number |  | HGV - Artic | Number / day
Coach parking spaces |  | Number |  | HGV - Rigid | Number / day
Other equipment |  | Unit | Reference
Crane - Rubber Tyred Gantry |  | Number |  | Optional inputs
Crane - Mobile harbour |  | Number
Crane - Ship-to-shore |  | Number |  | Peak power | Unit | Reference
Trailers |  | Number |  | Total port tenant peak power | kW
Tractors |  | Number |  | Rail infrastrucutre | kW
Forklifts |  | Number |  | Specialist equipment 1 | kW
Refrigerated containers |  | Number |  | Specialist equipment 2 | kW
|  |  |  | Specialist equipment 3 | kW
Hydrogen |  | Unit | Reference | Specialist equipment 4 | kW
Hydrogen production onsite for vessel refuelling | Yes | Yes / No |  | Specialist equipment 5 | kW
|  |  |  | Specialist equipment 6 | kW
N.B. Input an estmate of how much of the port is used at its businest times (this value would typically be below 80-90%) |  |  |  | Specialist equipment 7 | kW
Operation |  | Unit | Reference | Specialist equipment 8 | kW
Port operating capacity | 80% |  |  | Specialist equipment 9 | kW
1. Introduction
3. Assumptions
7. Function outputs
8. Outputs
6. Functions
5. Assumed constants
4. User inputs
2. Instructions

## 5. Assumed constants
Port asset power rating | [8 empty] | Electrification rate | [8 empty] | H2 / NH3 uptake rate
Berth type | Vessel charger power rating | Unit | Reference | Shore-to-ship power rating | Unit | Reference |  |  |  |  | 2021 | 2025 | 2030 | 2035 | 2040 | Reference |  |  |  | 2021 | 2025 | 2030 | 2035 | 2040 | Reference
Dry Bulk | 0 | n/a | EMSA 2020 | 7500 | kW | BPA 2020 |  |  | Vessel charging | Dry Bulk | 0% | 0% | 0% | 0% | 0% |  | n/a | H2 / NH3 fuel ready | Dry Bulk | 0% | 0% | 3% | 5% | 15% | ABS 2020
Liquid Bulk | 0 | n/a | EMSA 2020 | 10000 | kW | BPA 2020 |  |  |  | Liquid Bulk | 0% | 0% | 0% | 0% | 0% |  | n/a |  | Liquid Bulk | 0% | 0% | 3% | 5% | 15% | ABS 2020
Container Lo-Lo | 0 | n/a | EMSA 2020 | 8000 | kW | ICCT 2015 |  |  |  | Container Lo-Lo | 0% | 0% | 0% | 0% | 0% |  | n/a |  | Container Lo-Lo | 0% | 0% | 3% | 5% | 15% | ABS 2020
Other General Cargo | 0 | n/a | EMSA 2020 | 7500 | kW | BPA 2020 |  |  |  | Other General Cargo | 0% | 0% | 0% | 0% | 0% |  | n/a |  | Other General Cargo | 0% | 0% | 3% | 5% | 15% | ABS 2020
Ro-Ro (vehicle carriers) | 0 | n/a | EMSA 2020 | 6500 | kW | BPA 2020 |  |  |  | Ro-Ro (vehicle carriers) | 0% | 0% | 0% | 0% | 0% |  | n/a |  | Ro-Ro (vehicle carriers) | 0% | 0% | 3% | 5% | 15% | ABS 2020
Ro-Ro (unaccompanied) | 10000 | kW | EMSA 2020 | 3000 | kW | WBCSD2020 |  |  |  | Ro-Ro (unaccompanied) | 0% | 15% | 40% | 70% | 100% | TEN2020 |  |  | Ro-Ro (unaccompanied) | 0% | 0% | 0% | 0% | 0% | TEN2020 | n/a
Ferry / RoPAX | 10000 | kW | EMSA 2020 | 3000 | kW | WBCSD2020 |  |  |  | Ferry / RoPAX | 0% | 15% | 40% | 70% | 100% | TEN2020 |  |  | Ferry / RoPAX | 0% | 0% | 0% | 0% | 0% | TEN2020 | n/a
Cruise | 0 | n/a | EMSA 2020 | 20000 | kW | ICCT 2015 |  |  |  | Cruise | 0% | 0% | 0% | 0% | 0% |  | n/a |  | Cruise | 0% | 0% | 3% | 5% | 15% | ABS 2020
Reefers | 0 | n/a | EMSA 2020 | 16000 | kW | BPA 2020 |  |  |  | Reefers | 0% | 0% | 0% | 0% | 0% |  | n/a |  | Reefers | 0% | 0% | 3% | 5% | 15% | ABS 2020
Crew Transfer Vessels | 10000 | kW | EMSA 2020 | 2000 | kW | Assumed |  |  |  | Crew Transfer Vessels | 0% | 15% | 40% | 70% | 100% | TEN2020 |  |  | Crew Transfer Vessels | 0% | 0% | 0% | 0% | 0% | TEN2020 | n/a
Offshore Support Vessels | 0 | n/a | EMSA 2020 | 500 | kW | BPA 2020 |  |  |  | Offshore Support Vessels | 0% | 0% | 0% | 0% | 0% |  | n/a |  | Offshore Support Vessels | 0% | 0% | 3% | 5% | 15% | ABS 2020
Pilot boats & harbour craft | 10000 | kW | Assumed | 500 | kW | Assumed |  |  |  | Pilot boats & harbour craft | 0% | 15% | 40% | 70% | 100% | Assumed |  |  | Pilot boats & harbour craft | 0% | 0% | 0% | 0% | 0% | Assumed
Rigs | 10000 | kW | Assumed | 500 | kW | Assumed |  |  |  | Rigs | 0% | 15% | 40% | 70% | 100% | Assumed |  |  | Rigs | 0% | 0% | 0% | 0% | 0% | Assumed
[19 empty] | HGV - Arctic | 0% | 0% | 5% | 20% | 40% | NG Tool
Vehicles | Charger power rating | Unit | Reference | [5 empty] | Vehicle charging | Coach parking spaces with charging | 0% | 5% | 30% | 65% | 90% | TEN2020 |  |  | HGV - Rigid | 0% | 0% | 5% | 20% | 40% | NG Tool
Coach | 600 | kW | Siemens 2021 | [6 empty] | Car parking spaces with charging | 0% | 5% | 30% | 65% | 90% | TEN2020 |  |  | Proportion of vessels refuelling at port | 30% | 30% | 30% | 30% | 30% | NG Tool
Car | 160 | kW | Siemens 2020 | [6 empty] | Trailer | 0% | 5% | 30% | 65% | 90% | Assumed |  |  | Proportion of HGV refuelling at port | 50% | 50% | 50% | 50% | 50% | NG Tool
Trailer | 300 | kW | Siemens 2021 | [6 empty] | Tractor | 0% | 5% | 30% | 65% | 90% | Assumed
Tractors | 300 | kW | Siemens 2021 | [6 empty] | Forklift | 0% | 5% | 30% | 65% | 90% | Assumed
Forklifts | 30 | kW | EPRI 2015
HGV - Arctic | 0 | kW |  | n/a |  |  |  |  | Shore-to-ship | Dry Bulk | 1% | 5% | 15% | 25% | 60% | NG Tool
HGV - Rigid | 0 | kW |  | n/a | [5 empty] | Liquid Bulk | 1% | 5% | 15% | 25% | 60% | NG Tool
[10 empty] | Container Lo-Lo | 1% | 5% | 35% | 50% | 80% | NG Tool
Other equipment | Power rating | Unit | Reference | [6 empty] | Other General Cargo | 1% | 5% | 35% | 50% | 80% | NG Tool
Crane - Rubber Tyred Gantry | 506 | kW | LIEB 2020 | [6 empty] | Ro-Ro (vehicle carriers) | 1% | 5% | 35% | 50% | 80% | NG Tool
Crane - Ship-to-shore | 469 | kW | NG Tool | [6 empty] | Ro-Ro (unaccompanied) | 1% | 5% | 50% | 80% | 100% | NG Tool
Crane - Mobile harbour | 750 | kW | LIEBMHC 2020 | [6 empty] | Ferry / RoPAX | 0% | 30% | 100% | 100% | 100% | TE 2021
Refrigerated container | 10.8 | kW | CT 2018 | [6 empty] | Cruise | 0% | 30% | 100% | 100% | 100% | TE 2021
[10 empty] | Reefers | 1% | 5% | 35% | 50% | 80% | Assumed
[10 empty] | Crew Transfer Vessels | 1% | 5% | 35% | 50% | 80% | Assumed
Buildings | [9 empty] | Offshore Support Vessels | 1% | 5% | 35% | 50% | 80% | Assumed
Total building power demand / total site power demand | 2% | % | Assumed | [6 empty] | Pilot boats & harbour craft | 1% | 5% | 35% | 50% | 80% | Assumed
[10 empty] | Rigs | 1% | 5% | 35% | 50% | 80% | Assumed
[9 empty] | Other equipment | Crane - Rubber Tyred Gantry | 10% | 15% | 50% | 80% | 100% | NG Tool
[10 empty] | Crane - Ship-to-shore | 100% | 100% | 100% | 100% | 100% | NG Tool
[10 empty] | Crane - Mobile harbour | 0% | 5% | 35% | 50% | 80% | NG Tool
[10 empty] | Refrigerators | 100% | 100% | 100% | 100% | 100%
Fuel requirements
Vessels | Tank capacity | Unit | Reference | Conversion | Unit | Fuel type | Refuelling requirement | Reference
Dry Bulk | 6300000 | US Gallons | WSDoE1994 | 23845.5 | m3 | Marine deisel | 90% | Assumed
Liquid Bulk | 8400000 | US Gallons | WSDoE1994 | 31794 | m3 | Marine deisel | 90% | Assumed
Container Lo-Lo | 672000 | US Gallons | WSDoE1994 | 2543.52 | m3 | Marine deisel | 90% | Assumed
Other General Cargo | 840000 | US Gallons | WSDoE1994 | 3179.4 | m3 | Marine deisel | 90% | Assumed
Ro-Ro (vehicle carriers) | 3550 | m3 | CSB2020 | 3550 | m3 | Marine deisel | 90% | Assumed
Ro-Ro (unaccompanied) | 2000 | m3 | Assumed | 2000 | m3 | Marine deisel | 40% | Assumed
Ferry / RoPAX | 1000 | m3 | CSB2020 | 1000 | m3 | Marine deisel | 40% | Assumed
Cruise | 2000000 | US Gallons | WSDoE1994 | 7570 | m3 | Marine deisel | 90% | Assumed
Reefers | 1669 | m3 | HijosDJ2021 | 1669 | m3 | Marine deisel | 90% | Assumed
Crew Transfer Vessels | 14000 | Litres | CWind2020 | 14 | m3 | Marine deisel | 40% | Assumed
Offshore Support Vessels | 12000 | Litres | JFMS2021 | 12 | m3 | Marine deisel | 50% | Assumed
Pilot boats & harbour craft | 12000 | Litres | Assumed | 12 | m3 | Marine deisel | 50% | Assumed
Rigs | 12000 | Litres | Assumed | 12 | m3 | Marine deisel | 50% | Assumed
Vehicles | Deisel (per vehicle) | Unit | Reference | Conversion | Unit | Fuel type | Refuelling requirement | Reference
HGV - Artic | 1475 | Litres | Renault 2013 | 1.475 | m3 | HGV diesel | 75% | Assumed
HGV - Rigid | 450 | Litres | DAF 2021 | 0.45 | m3 | HGV diesel | 75% | Assumed
Conversion factors | Value | Unit | Reference
HGV diesel (m3) : H2/NH3 (m3) | 4.58 |  | EFTE2018
Marine diesel (m3) : H2/NH3 (m3) | 4.58 |  | EFTE2018
US Gallon to m3 | 0.003785
Liter to m3 | 0.001
H2 production energy consumption | 52 | kWhe / kg | IRENA 2018
H2 liquification energy consumption | 12 | kWhe / kg | IDEALHY 2013
Liquid Hydrogen conversion | 71 | kg / m3 | EFTE 2018
H2 production | Value | Unit | Reference
Proportion of H2 production onsite | 10% |  | Assumed
H2 plant operating profile | 20 | hours / day | IRENA 2018
1. Introduction
3. Assumptions
7. Function outputs
8. Outputs
6. Functions
5. Assumed constants
4. User inputs
2. Instructions

## 6. Functions
2021 asset peak power |  |  |  | 2021 hydrogen plant peak power
|  | Vessel chargers (kW) | Shore-to-ship (kW) | Max diesel requirement / day (m3) | Actual diesel requirement / day (m3) | Max H2 requirement / day (m3) | Actual H2 requirement / day (m3) | H2 produced at port / day (m3) | H2 produced at port / day (kg) | Total energy required - production / day (kWh) | Total energy requirement - liquification / day (kWh) | Total energy / day (kWh)
Vessel / berth | Dry Bulk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Liquid Bulk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Container Lo-Lo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other General Cargo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ro-Ro (vehicle carriers) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ro-Ro (unaccompanied) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ferry / RoPAX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cruise | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reefers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Crew Transfer Vessels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Offshore Support Vessels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pilot boats & harbour craft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rigs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak power (kW)
Vehicle | Coach chargers | 0
| Car chargers | 0
| HGV - Arctic |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HGV - Rigid |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other equipment | eTrailer chargers | 0
| eTractor chargers | 0
| eForklift chargers | 0
| Crane - Rubber Tyred Gantry | 0
| Crane - Mobile harbour | 0
| Crane - Ship-to-shore | 0
| Port tenant (e.g. industrial processes) | 0
| Rail infrastrucutre | 0
| Buildings | 0
| Refridgerated containters | 0
| Specialist equipment | 0
[8 empty] | Total energy / day (kWh) |  |  |  | 0
[8 empty] | Plant peak power (kW) |  |  |  | 0
[8 empty] | Plant peak power (MW) |  |  |  | 0
2025 asset peak power |  |  |  | 2025 hydrogen plant peak power
|  | Vessel chargers (kW) | Shore-to-ship (kW) | Max diesel requirement / day (m3) | Actual diesel requirement / day (m3) | Max H2 requirement / day (m3) | Actual H2 requirement / day (m3) | H2 produced at port / day (m3) | H2 produced at port / day (kg) | Total energy required - production / day (kWh) | Total energy requirement - liquification / day (kWh) | Total energy / day (kWh)
Vessel / berth | Dry Bulk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Liquid Bulk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Container Lo-Lo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other General Cargo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ro-Ro (vehicle carriers) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ro-Ro (unaccompanied) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ferry / RoPAX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cruise | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reefers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Crew Transfer Vessels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Offshore Support Vessels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pilot boats & harbour craft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rigs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak power (kW)
Vehicle | Coach chargers | 0
| Car chargers | 0
| HGV - Arctic |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HGV - Rigid |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other equipment | eTrailer chargers | 0
| eTractor chargers | 0
| eForklift chargers | 0
| Crane - Rubber Tyred Gantry | 0
| Crane - Mobile harbour | 0
| Crane - Ship-to-shore | 0
| Port tenant (e.g. industrial processes) | 0
| Rail infrastrucutre | 0
| Buildings | 0
| Refridgerated containters | 0
| Specialist equipment | 0
[8 empty] | Total energy / day (kWh) |  |  |  | 0
[8 empty] | Plant peak power (kW) |  |  |  | 0
[8 empty] | Plant peak power (MW) |  |  |  | 0
2030 asset peak power |  |  |  | 2030 hydrogen plant peak power
|  | Vessel chargers (kW) | Shore-to-ship (kW) | Max diesel requirement / day (m3) | Actual diesel requirement / day (m3) | Max H2 requirement / day (m3) | Actual H2 requirement / day (m3) | H2 produced at port / day (m3) | H2 produced at port / day (kg) | Total energy required - production / day (kWh) | Total energy requirement - liquification / day (kWh) | Total energy / day (kWh)
Vessel / berth | Dry Bulk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Liquid Bulk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Container Lo-Lo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other General Cargo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ro-Ro (vehicle carriers) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ro-Ro (unaccompanied) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ferry / RoPAX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cruise | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reefers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Crew Transfer Vessels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Offshore Support Vessels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pilot boats & harbour craft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rigs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak power (kW)
Vehicle | Coach chargers | 0
| Car chargers | 0
| HGV - Arctic |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HGV - Rigid |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other equipment | eTrailer chargers | 0
| eTractor chargers | 0
| eForklift chargers | 0
| Crane - Rubber Tyred Gantry | 0
| Crane - Mobile harbour | 0
| Crane - Ship-to-shore | 0
| Port tenant (e.g. industrial processes) | 0
| Rail infrastrucutre | 0
| Buildings | 0
| Refridgerated containters | 0
| Specialist equipment | 0
[8 empty] | Total energy / day (kWh) |  |  |  | 0
[8 empty] | Plant peak power (kW) |  |  |  | 0
[8 empty] | Plant peak power (MW) |  |  |  | 0
2035 asset peak power |  |  |  | 2035 hydrogen plant peak power
|  | Vessel chargers (kW) | Shore-to-ship (kW) | Max diesel requirement / day (m3) | Actual diesel requirement / day (m3) | Max H2 requirement / day (m3) | Actual H2 requirement / day (m3) | H2 produced at port / day (m3) | H2 produced at port / day (kg) | Total energy required - production / day (kWh) | Total energy requirement - liquification / day (kWh) | Total energy / day (kWh)
Vessel / berth | Dry Bulk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Liquid Bulk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Container Lo-Lo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other General Cargo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ro-Ro (vehicle carriers) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ro-Ro (unaccompanied) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ferry / RoPAX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cruise | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reefers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Crew Transfer Vessels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Offshore Support Vessels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pilot boats & harbour craft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rigs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak power (kW)
Vehicle | Coach chargers | 0
| Car chargers | 0
| HGV - Arctic |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HGV - Rigid |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other equipment | eTrailer chargers | 0
| eTractor chargers | 0
| eForklift chargers | 0
| Crane - Rubber Tyred Gantry | 0
| Crane - Mobile harbour | 0
| Crane - Ship-to-shore | 0
| Port tenant (e.g. industrial processes) | 0
| Rail infrastrucutre | 0
| Buildings | 0
| Refridgerated containters | 0
| Specialist equipment | 0
[8 empty] | Total energy / day (kWh) |  |  |  | 0
[8 empty] | Plant peak power (kW) |  |  |  | 0
[8 empty] | Plant peak power (MW) |  |  |  | 0
2040 asset peak power (kW) |  |  |  | 2040 hydrogen plant peak power
|  | Vessel chargers (kW) | Shore-to-ship (kW) | Max diesel requirement / day (m3) | Actual diesel requirement / day (m3) | Max H2 requirement / day (m3) | Actual H2 requirement / day (m3) | H2 produced at port / day (m3) | H2 produced at port / day (kg) | Total energy required - production / day (kWh) | Total energy requirement - liquification / day (kWh) | Total energy / day (kWh)
Vessel / berth | Dry Bulk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Liquid Bulk | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Container Lo-Lo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other General Cargo | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ro-Ro (vehicle carriers) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ro-Ro (unaccompanied) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ferry / RoPAX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cruise | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reefers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Crew Transfer Vessels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Offshore Support Vessels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pilot boats & harbour craft | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rigs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak power
Vehicle | Coach chargers | 0
| Car chargers | 0
| HGV - Arctic |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HGV - Rigid |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Other equipment | eTrailer chargers | 0
| eTractor chargers | 0
| eForklift chargers | 0
| Crane - Rubber Tyred Gantry | 0
| Crane - Mobile harbour | 0
| Crane - Ship-to-shore | 0
| Port tenant (e.g. industrial processes) | 0
| Rail infrastrucutre | 0
| Buildings | 0
| Refridgerated containters | 0
| Specialist equipment | 0
[8 empty] | Total energy / day (kWh) |  |  |  | 0
[8 empty] | Plant peak power (kW) |  |  |  | 0
[8 empty] | Plant peak power (MW) |  |  |  | 0
1. Introduction
3. Assumptions
7. Function outputs
8. Outputs
6. Functions
5. Assumed constants
4. User inputs
2. Instructions

## 7. Function outputs
Total peak power (kW)
|  | 2021 | 2025 | 2030 | 2035 | 2040
Port infractruture | Vessel chargers | 0 | 0 | 0 | 0 | 0
| Shore-to-ship | 0 | 0 | 0 | 0 | 0
| Car chargers | 0 | 0 | 0 | 0 | 0
| Coach chargers | 0 | 0 | 0 | 0 | 0
| eTrailer chargers | 0 | 0 | 0 | 0 | 0
| eTractor chargers | 0 | 0 | 0 | 0 | 0
| eForklift chargers | 0 | 0 | 0 | 0 | 0
| Buildings | 0 | 0 | 0 | 0 | 0
| Crane - Rubber Tyred Gantry | 0 | 0 | 0 | 0 | 0
| Crane - Mobile harbour | 0 | 0 | 0 | 0 | 0
| Crane - Ship-to-shore | 0 | 0 | 0 | 0 | 0
| Refrigerated container | 0 | 0 | 0 | 0 | 0
| H2 production plant | 0 | 0 | 0 | 0 | 0
Optional | Port tenant (e.g. industrial processes) | 0 | 0 | 0 | 0 | 0
| Rail infrastrucutre | 0 | 0 | 0 | 0 | 0
| Specialist equipment | 0 | 0 | 0 | 0 | 0
1. Introduction
3. Assumptions
7. Function outputs
8. Outputs
6. Functions
5. Assumed constants
4. User inputs
2. Instructions

## 8. Outputs
| Total port peak power (with Hydrogen production) | [5 empty] | Total port peak power (without Hydrogen production)
| 2021 | 2025 | 2030 | 2035 | 2040 |  | 2021 | 2025 | 2030 | 2035 | 2040
kW | 0 | 0 | 0 | 0 | 0 | kW | 0 | 0 | 0 | 0 | 0
MW | 0 | 0 | 0 | 0 | 0 | MW | 0 | 0 | 0 | 0 | 0
GW | 0 | 0 | 0 | 0 | 0 | GW | 0 | 0 | 0 | 0 | 0
| Base case | [5 empty] | Base case
National Grid guidance
2021 (baseload) | Connection solution: A Distribution Network Operator connection is considered more efficient for this level of demand. Advice: A discussion with Distribution Network Operator is suggested to check if remaining network capacity is available or any reinforcement works are required to accommodate your demand. Action: Discussion with your Distribution Network Operator. Submit connection application if required. Time to act: Now
2025 | Connection solution: A Distribution Network Operator connection is considered more efficient for this level of demand. Advice: A discussion with Distribution Network Operator is suggested to check if remaining network capacity is available or any reinforcement works are required to accommodate your demand. Action: Discussion with your Distribution Network Operator. Submit connection application if required. Time to act: Now
2030 | Connection solution: A Distribution Network Operator connection is considered more efficient for this level of demand. Advice: A discussion with Distribution Network Operator is suggested to check if remaining network capacity is available or any reinforcement works are required to accommodate your demand. Action: Discussion with your Distribution Network Operator. Submit connection application if required. Time to act: Now
2035 | Connection solution: A Distribution Network Operator connection is considered more efficient for this level of demand. Advice: A discussion with Distribution Network Operator is suggested to check if remaining network capacity is available or any reinforcement works are required to accommodate your demand. Action: Discussion with your Distribution Network Operator. Submit connection application if required. Time to act: Now
2040 | Connection solution: A Distribution Network Operator connection is considered more efficient for this level of demand. Advice: A discussion with Distribution Network Operator is suggested to check if remaining network capacity is available or any reinforcement works are required to accommodate your demand. Action: Discussion with your Distribution Network Operator. Submit connection application if required. Time to act: Now
1. Introduction
3. Assumptions
7. Function outputs
8. Outputs
6. Functions
5. Assumed constants
4. User inputs
2. Instructions

## NG outputs (hidden)
| Lower band (kW) | Upper band (kW) | National Grid comments
2021 | 1 | 50000 | Connection solution: A Distribution Network Operator connection is considered more efficient for this level of demand. Advice: A discussion with Distribution Network Operator is suggested to check if remaining network capacity is available or any reinforcement works are required to accommodate your demand. Action: Discussion with your Distribution Network Operator. Submit connection application if required. Time to act: Now
| 50000 | 100000 | Connection solution: Either a distribution or direct transmission connection could be most efficient depending on network conditions and development plans in your region. Advice: It's worthwhile evaluating both connection solutions with your current Distribution Network Operator connection provider and Transmission System Operator. Significant network reinforcement works might be involved which require multiple year delivery times. We therefore encourage you to contact Distribution Network Operator and Transmission System Operator as soon as possible. Action: Start the conversation with Transmission System Operator and Distribution Network Operator. Contact: box.DecarbTransport@nationalgrid.com. Submit connection application and develop site specific solution and delivery plan. Time to act: Five years before this date
| 100000 | infinite | Connection solution: A direct transmission connection is likely to be most efficient way to access grid supplied energy. Advice: Significant network reinforcement works might be involved which require multiple year delivery times. We therefore encourage you to contact Transmission System Operator as soon as possible. Action: Start the conversation with Transmission System Operator. Contact: box.DecarbTransport@nationalgrid.com. Submit connection application and develop site specific solution and delivery plan. Time to act: Five years before this date
2025 | 1 | 50000 | Connection solution: A Distribution Network Operator connection is considered more efficient for this level of demand. Advice: A discussion with Distribution Network Operator is suggested to check if remaining network capacity is available or any reinforcement works are required to accommodate your demand. Action: Discussion with your Distribution Network Operator. Submit connection application if required. Time to act: Now
| 50000 | 100000 | Connection solution: Either a distribution or direct transmission connection could be most efficient depending on network conditions and development plans in your region. Advice: It's worthwhile evaluating both connection solutions with your current Distribution Network Operator connection provider and Transmission System Operator. Significant network reinforcement works might be involved which require multiple year delivery times. We therefore encourage you to contact Distribution Network Operator and Transmission System Operator as soon as possible. Action: Start the conversation with Transmission System Operator and Distribution Network Operator. Contact: box.DecarbTransport@nationalgrid.com. Submit connection application and develop site specific solution and delivery plan. Time to act: Five years before this date
| 100000 | infinite | Connection solution: A direct transmission connection is likely to be most efficient way to access grid supplied energy. Advice: Significant network reinforcement works might be involved which require multiple year delivery times. We therefore encourage you to contact Transmission System Operator as soon as possible. Action: Start the conversation with Transmission System Operator. Contact: box.DecarbTransport@nationalgrid.com. Submit connection application and develop site specific solution and delivery plan. Time to act: Five years before this date
2030 | 1 | 50000 | Connection solution: A Distribution Network Operator connection is considered more efficient for this level of demand. Advice: A discussion with Distribution Network Operator is suggested to check if remaining network capacity is available or any reinforcement works are required to accommodate your demand. Action: Discussion with your Distribution Network Operator. Submit connection application if required. Time to act: Now
| 50000 | 100000 | Connection solution: Either a distribution or direct transmission connection could be most efficient depending on network conditions and development plans in your region. Advice: It's worthwhile evaluating both connection solutions with your current Distribution Network Operator connection provider and Transmission System Operator. Significant network reinforcement works might be involved which require multiple year delivery times. We therefore encourage you to contact Distribution Network Operator and Transmission System Operator as soon as possible. Action: Start the conversation with Transmission System Operator and Distribution Network Operator. Contact: box.DecarbTransport@nationalgrid.com. Submit connection application and develop site specific solution and delivery plan. Time to act: Five years before this date
| 100000 | infinite | Connection solution: A direct transmission connection is likely to be most efficient way to access grid supplied energy. Advice: Significant network reinforcement works might be involved which require multiple year delivery times. We therefore encourage you to contact Transmission System Operator as soon as possible. Action: Start the conversation with Transmission System Operator. Contact: box.DecarbTransport@nationalgrid.com. Submit connection application and develop site specific solution and delivery plan. Time to act: Five years before this date
2035 | 1 | 50000 | Connection solution: A Distribution Network Operator connection is considered more efficient for this level of demand. Advice: A discussion with Distribution Network Operator is suggested to check if remaining network capacity is available or any reinforcement works are required to accommodate your demand. Action: Discussion with your Distribution Network Operator. Submit connection application if required. Time to act: Now
| 50000 | 100000 | Connection solution: Either a distribution or direct transmission connection could be most efficient depending on network conditions and development plans in your region. Advice: It's worthwhile evaluating both connection solutions with your current Distribution Network Operator connection provider and Transmission System Operator. Significant network reinforcement works might be involved which require multiple year delivery times. We therefore encourage you to contact Distribution Network Operator and Transmission System Operator as soon as possible. Action: Start the conversation with Transmission System Operator and Distribution Network Operator. Contact: box.DecarbTransport@nationalgrid.com. Submit connection application and develop site specific solution and delivery plan. Time to act: Five years before this date
| 100000 | infinite | Connection solution: A direct transmission connection is likely to be most efficient way to access grid supplied energy. Advice: Significant network reinforcement works might be involved which require multiple year delivery times. We therefore encourage you to contact Transmission System Operator as soon as possible. Action: Start the conversation with Transmission System Operator. Contact: box.DecarbTransport@nationalgrid.com. Submit connection application and develop site specific solution and delivery plan. Time to act: Five years before this date
2040 | 1 | 50000 | Connection solution: A Distribution Network Operator connection is considered more efficient for this level of demand. Advice: A discussion with Distribution Network Operator is suggested to check if remaining network capacity is available or any reinforcement works are required to accommodate your demand. Action: Discussion with your Distribution Network Operator. Submit connection application if required. Time to act: Now
| 50000 | 100000 | Connection solution: Either a distribution or direct transmission connection could be most efficient depending on network conditions and development plans in your region. Advice: It's worthwhile evaluating both connection solutions with your current Distribution Network Operator connection provider and Transmission System Operator. Significant network reinforcement works might be involved which require multiple year delivery times. We therefore encourage you to contact Distribution Network Operator and Transmission System Operator as soon as possible. Action: Start the conversation with Transmission System Operator and Distribution Network Operator. Contact: box.DecarbTransport@nationalgrid.com. Submit connection application and develop site specific solution and delivery plan. Time to act: Five years before this date
| 100000 | infinite | Connection solution: A direct transmission connection is likely to be most efficient way to access grid supplied energy. Advice: Significant network reinforcement works might be involved which require multiple year delivery times. We therefore encourage you to contact Transmission System Operator as soon as possible. Action: Start the conversation with Transmission System Operator. Contact: box.DecarbTransport@nationalgrid.com. Submit connection application and develop site specific solution and delivery plan. Time to act: Five years before this date