## Example 1 - Existing Intertrips
Example 1: Derogated Boundary with existing commercial intertrips
Required Capability (2009/10): | 4000 |  | Maximum Allowed Intertrip Capability: |  |  | 1320
Actual Capability (2009/10): | 2200 |  | Total Available Intertrip Capability: |  |  | 4050
Difference: | 1800
POWER STATION | A | B | C | D | E | F | G
| 4 x 350 MW coal fired power station, existing commercial intertrip | 4 x 500 MW coal fired power station | 1 x 800 MW CCGT power station, existing commercial intertrip | 4 x 650 MW nuclear power station, existing commercial intertrip | 4 x 200 MW hydro power station | 150 MW wind farm | 100 MW wind farm
a) Total Station Output Capable of Being Intertripped | 1400 | 2400 | 250 | 2600 | 800 | 150 | 50
b) The cost of connecting a Generating Unit to the System-to-Generator Scheme | 0 | 200000 | 0 | 0 | 200000 | 200000 | 200000
c) Payments associated with a category 5 service provider | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000
d) Trippable size of individual Generating Unit | 350 | 600 | 250 | 650 | 200 | 150 | 50
e) Load factor | 0.625 | 0.625 | 0.632 | 0.596 | 0.161 | 0.26 | 0.26
f) BMU Output x Load Factor (d*e) | 218.75 | 375 | 158 | 387.4 | 32.2 | 39 | 13
g) Total Station x Load Factor (a*e) | 875 | 1500 | 158 | 1549.6 | 128.8 | 39 | 13
h) (1) Effective Cost per Generating Unit (£/MWh) (b+c)/(f) | 137.1429 | 613.3333 | 189.8734 | 77.4393 | 7142.8571 | 5897.4359 | 17692.3077
h) (2) Effective Cost for Power Station (£/MWh) (b+c)/(g) | 34.2857 | 153.3333 | 189.8734 | 19.3598 | 1785.7143 | 5897.4359 | 17692.3077
i) Firm trippable Generation: Total Station x Load Factor - BMU Outage (g-d) | 525 | 900 | -92 | 899.6 | -71.2 | -111 | -37
Other factors to consider
j) Anticipated time to return to commercial load following an intertrip; | 6 hours | 6 hours | 10 hours | 999 min (max allowed) | 999 min (max allowed) | Up to 1 hour | Up to 30 min
k) Technical characteristics of a Generating Unit;
l) For a boundary which requires 1320 MW on intertrip, how much volume of intertrip should be available? | Diversity is required to ensure intertrip capability exists during generating unit outages and a range of energy market conditions.The capability to trip up to 1320 MW must continue to exist, taking account of station load factors and the need for planned BMU outages. Using the firm trippable generation levels above, power stations A and D would be chosen to provide Category 5 intertrips. The total volume of intertrip availability would be 4000 MW, being the combined station output of A and D.
Power Stations selected for Category 5 Intertrip: | X (All Units) |  |  | X (All Units)
a) For Station C, 250 MW represents 1 x GT. BMU has 2 x 250 MW GTs and 1 x 300 MW ST). Assumes CCGT has demonstrated contractual obligation to deliver steam, hence can only trip 1 GT (0 GTs during GT outages)
b) £200,000 assumed for installation of new intertrip equipment
c) Standard annual capability fee as per CUSC
e) Based on publicly available data from DECC/BERR (Dukes)
g) Need to maintain 1320 MW intertrip capability during outage of one BMU per station
i) Initial selection shown with BOLD border
j) MZT data from BMRS (www.bmreports.com)

## Example 2 - No Intertrips
Example 2: Derogated Boundary with no existing commercial intertrips
Required Capability (2009/10): | 4000 |  | Maximum Allowed Intertrip Capability: |  |  | 1320
Actual Capability (2009/10): | 2200 |  | Total Available Intertrip Capability: |  |  | 4050
Difference: | 1800
POWER STATION | A | B | C | D | E | F | G
| 4 x 350 MW coal fired power station | 4 x 500 MW coal fired power station | 1 x 800 MW CCGT power station | 4 x 650 MW nuclear power station | 4 x 200 MW hydro power station | 150 MW wind farm | 100 MW wind farm
a) Total Station Output Capable of Being Intertripped | 1400 | 2400 | 250 | 2600 | 800 | 150 | 50
b) The cost of connecting a Generating Unit to the System-to-Generator Scheme | 200000 | 200000 | 200000 | 200000 | 200000 | 200000 | 200000
c) Payments associated with a category 5 service provider | 30000 | 30000 | 30000 | 30000 | 30000 | 30000 | 30000
d) Trippable size of individual Generating Unit | 350 | 600 | 250 | 650 | 200 | 150 | 50
e) Load factor | 0.625 | 0.625 | 0.632 | 0.596 | 0.161 | 0.26 | 0.26
f) BMU Output x Load Factor (d*e) | 218.75 | 375 | 158 | 387.4 | 32.2 | 39 | 13
g) Total Station x Load Factor (a*e) | 875 | 1500 | 158 | 1549.6 | 128.8 | 39 | 13
h) (1) Effective Cost per Generating Unit (£/MWh) (b+c)/(f) | 1051.4286 | 613.3333 | 1455.6962 | 593.7016 | 7142.8571 | 5897.4359 | 17692.3077
h) (2) Effective Cost for Power Station (£/MWh) (b+c)/(g) | 262.8571 | 153.3333 | 1455.6962 | 148.4254 | 1785.7143 | 5897.4359 | 17692.3077
i) Firm trippable Generation: Total Station x Load Factor - BMU Outage (g-d) | 525 | 900 | -92 | 899.6 | -71.2 | -111 | -37
Other factors to consider
j) Anticipated time to return to commercial load following an intertrip; | 6 hours | 6 hours | 10 hours | 999 min (max allowed) | 999 min (max allowed) | Up to 1 hour | Up to 30 min
k) Technical characteristics of a Generating Unit; | With no pre-existing commercial intertrips, the effectiveness of nuclear plant remains high, although the likely timescales associated with making changes to the Safety Case count against it in terms of selection as, over the lifetime of the derogation, other alternatives are likely to be more attractive.
l) For a boundary which requires 1320 MW on intertrip, how much volume of intertrip should be available? | Diversity is required to ensure intertrip capability exists during generating unit outages and a range of energy market conditions.The capability to trip up to 1320 MW must continue to exist, taking account of station load factors and the need for planned BMU outages. Using the effectiveness and the firm trippable generation levels above, power stations A and B would be chosen to provide Category 5 intertrips. The total volume of intertrip availability would be 3800 MW, being the combined station output of A and B.
Power Stations selected for Category 5 Intertrip: | X (All Units) | X (All Units)
a) For Station C, 250 MW represents 1 x GT. BMU has 2 x 250 MW GTs and 1 x 300 MW ST). Assumes CCGT has demonstrated contractual obligation to deliver steam, hence can only trip 1 GT (0 GTs during GT outages)
b) £200,000 assumed for installation of new intertrip equipment
c) Standard annual capability fee as per CUSC
e) Based on publicly available data from DECC/BERR (Dukes)
g) Need to maintain 1320 MW intertrip capability during outage of one BMU per station
i) Initial selection shown with BOLD border
j) MZT data from BMRS (www.bmreports.com)

## Arming Example
ARMING EXAMPLE
Assume non I/T limit = 2000MW, anticipated flow = 2400MW
Note that this Arming example is separate to the Selection examples. Stations A to D in the table below have Category 5 intertrips installed, and the selection criteria are based on close-to-real-time considerations. It is assumed that all generating units will be running.
| A | B | C | D
a) The output of category 5 providers’ generating units; | 300 | 500 | 600 | 400
b) The effectiveness of intertripping a specific unit in relieving the constraint with respect to the conditions at that time; | increases limit by: 250MW | increases limit by: 400MW | increases limit by: 400MW | increases limit by: 300MW
c) Any disproportionately detrimental effect to the system in the event of a specific generating unit or combination of units being intertripped when compared to the benefit of arming that generating unit or units (e.g. impact of loss of MVAr reserves, local constraint issues); | Unit providing voltage support for next credible fault | None specific | Long time to resync (Minimum Zero Time) following trip | None specific
(d) Where practicable, only arming sufficient intertrip volume on generating units to enable the discrepancy between the present derogated transmission boundary capability and that capability that would be required to satisfy compliance with the GB SQSS; and | 300MW benefit required: 250MW delivered by arming this unit | 400MW benefit required: 400MW benefit delivered by arming this unit | 400MW benefit required: 400MW benefit delivered by arming this unit | 400MW benefit required: 300MW benefit delivered by arming this unit
(e) Equitable treatment of generating units where more than one generating unit can provide the required intertrip volume and where, after taking into consideration the above criteria, there is no way of differentiating between the generating units. | Not relevant in this example
Summary | under provides, and required for volts | satisfactorily provides: no specific detriment | satisfactorily provides but long MZT if tripped | under provides
Therefore, in this example, most suitable candidates for arming are Units B and C, with preference to arm B owing to long NDZ for unit C.