## Generator
TWR Report
Company Name | Generator Name | Scheme Number | Connection Site | Scheme Description | Connection Date
Aberarder Wind Farm LLP | Aberarder Wind Farm | Aberarder item 1 | Aberarder 132/33Kv Substation | Establishment of approx. 5km of new single circuit 132kV wood pole trident line between the proposed wind farm substation at Aberarder and the Dunmaglass-Farigaig 132kV overhead line circuit. At Aberarder wind farm substation, the 132kV overhead circuit will terminate on to a new 132kV circuit switcher (115) to be established within the substation compound. At Dunmaglass - Farigaig side the overhead line circuit will terminate via a 132kV circuit switcher (125) to be established within a switching compound to be established adjacent to the existing Dunmaglass-Farigaig overhead line. The circuit switcher 125 will tee into the Dunmaglass-Farigaig circuit at this point. | 30/06/2020
|  | SHETL-RI-089 | Aberarder 132/33Kv Substation | Upgrade the 120MVA 275/132kV SGT1 at Farigaig substation to a 240MVA SGT to facilitate the connection of generation in the area. | 30/06/2020
|  | SHETL-RI-007C | Aberarder 132/33Kv Substation | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | 30/06/2020
Aberdeen Offshore Wind Farm Limited | Aberdeen Offshore Wind Farm |  | Blackdog 132kV Substation | The works include installation of a new 132kV feeder circuit breaker at the existing Dyce 132kV substation, complete with 132kV busbar disconnector and 132kV line circuit breaker. The works at the existing Dyce 132kV substation also include the installation of 132kV transformer circuit switcher on the existing grid transformer GT1. | 01/04/2018
|  |  | Blackdog 132kV Substation | The replacement of section tower near the tail end of double circuit tower line (XPN/XPS) at Stoneyhill and the installation of 9.5km of 132kV underground cable from 132kV circuit XPS at Stoneyhill to the new 132kV substation building at the user's landfall site. At the landfall substation, the 132kV substation building at the user's landfall site. At the landfall substation, the 132kV underground cable will terminate onto a 132kV GIS line disconnector located within the substation building. The cabling will comprise three single core XLPE Cu 630mm cables to meet the wind farm capacity. | 01/04/2018
|  |  | Blackdog 132kV Substation | Modification of existing protection and telecommunications equipment at Kintore and Dyce 132kV substations to suit the new Aberdeen Offshore connection arrangement. | 01/04/2018
|  | SPT-RI-101 | Blackdog 132kV Substation | Construct double circuit 132kV overhead line from New Cumnock 132kV substation to the new Windy Standard Collector Substation and at New Cumnock establish two new 132kV circuit breaker bays to facilitate the connection of the new circuits. | 01/04/2018
Abernedd Power Company Ltd | Abernedd Power Station | 32313SI | Baglan Bay 275kV | Uprate the existing switchgear at Margam 275kV substation. Replace circuit breaker 2T0 at Margam 66kV substation | 31/10/2026
|  | Thermal uprate of the Cardiff East – Uskmouth – Whitson circuit | Baglan Bay 275kV | Thermal uprate of the Cardiff East – Uskmouth – Whitson circuit | 31/10/2026
|  | Thermal uprate of the circuits from Whitson – Iron Acton – Melksham | Baglan Bay 275kV | Thermal uprate of the circuits from Whitson – Iron Acton – Melksham | 31/10/2026
|  | Thermal uprate of Whitson SGT5 | Baglan Bay 275kV | Thermal uprate of Whitson SGT5 | 31/10/2026
|  | Thermal uprate of the Cardiff East leg of the Pyle – Aberthaw – Cardiff East circuit | Baglan Bay 275kV | Thermal uprate of the Cardiff East leg of the Pyle – Aberthaw – Cardiff East circuit | 31/10/2026
|  | 20736 | Baglan Bay 275kV | Install a new 1100MVA 400/275kV transformer and bank this with the existing Swansea North SGT9 | 31/10/2026
|  | 33730 | Baglan Bay 275kV | Extend the existing Baglan Bay 275kV substation to accommodate a new GIS generator bay. Install a generator to system intertrip scheme. Uprate the existing switchgear at Pyle 275kV substation | 31/10/2026
|  | Thermal uprate of the Cowley – Walham circuit | Baglan Bay 275kV | Thermal uprate of the Cowley – Walham circuit | 31/10/2026
|  | Thermal uprate of the Uskmouth – Whitson 2 circuit | Baglan Bay 275kV | Thermal uprate of the Uskmouth – Whitson 2 circuit | 31/10/2026
|  | Thermal uprate of the Imperial Park – Melksham and the Cilfynydd – Whitson – Seabank circuit | Baglan Bay 275kV | Thermal uprate of the Imperial Park – Melksham and the Cilfynydd – Whitson – Seabank circuit (Severn Cable circuits) | 31/10/2026
|  | Thermal uprate of the Aberthaw – Tremorfa circuit | Baglan Bay 275kV | Thermal uprate of the Aberthaw – Tremorfa circuit | 31/10/2026
Western Power Distribution (South West) Plc | Abham | NGET-RI-30752 |  | Creation of a new South West Operational Tripping Scheme (OTS) at Taunton.
|  | NGET-RI-31671-1 |  | Re-conductor the Bramley - Fleet OHL circuits to increase capacity.
|  | NGET-RI-31671-2 |  | Re-conductor the Fleet - Lovedean OHL circuits to increase capacity.
|  | NGET-RI-33539 |  | Hot wiring of the Hinckley Point - Melksham 1 and 2 circuits to increase their thermal rating.
Achlachan Wind Farm LLP | Achlachan | SHETL-RI-032B |  | Reinforce the existing 132kV double circuit overhead line between Dounreay, Thurso and Mybster substation (UTN/UTS and part of TME/TMW) Via a new 275/132kV substation at Spittal.
|  | SHETL-RI-035 |  | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs.
|  | SHETL-RI-036 |  | Reconductor part of the first 275kV circuits (BT1 - Beauly - Kilbraur - Gordonbush - Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substation (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay.
|  | SHETL-RI-037 |  | Establish a new 275/132kV Fyrish substation close to the existing Alness 132kV OHL Tee location. The substation shall interface with the 275kV double-circuit between Beauly and Loch Buidhe. An optimal 132kV route will be designed and engineered to link the new 275/132kV Fyrish substation with the existing Alness GSP.
|  | SHETL-RI-002 & SPT-RI-001A |  | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation.
|  | Achlachan Item 12 |  | The User has requested non-firm access ahead of completion of the required transmission enabling works, SHET-RI-058 and SHETL-RI-060. This will require the implementation of an Intertrip scheme to disconnect the output of the windfarm from the network via the relevant circuit breaker, when the new HVDC link between Spittal substation (Caithness) and Blackhillock substation (Morayshire) is unavailable. These works therefore cover the design, installation and commissioning of a temporary Intertrip scheme to give access to the transmission system by the User’s agreed connection date of 31st October 2018.
|  | SHETL-RI-032A |  | A new 275kV overhead line and substation works between Dounreay, Thurso and Spittal Substations.
|  | Achlachan Item 2 |  | Install 2 x 132kV transformer circuit breaker bays connected off the Mybster 132kV busbar extension, complete with protection and associated auxiliary equipment. (The incumbent 33kV switchboard and 132kV transformer circuit switchers are adequately rated to meet the 120MVA transformer capacity; hence no further works are required)
|  | Achlachan Item 1 |  | At Mybster 132/33kV substation, the Relevant Transmission Licensee shall replace the existing 2 x 30 MVA and 1 x 60 MVA 132/33kV transformers with higher rated twin 120MVA 132/33kV transformers within the same substation accommodation. The works will include all associated plinth foundations, transformer protection equipment, and 33kV cabling work associated with the two replacement 120MVA transformers.
|  | Achlachan Item 3 |  | Install 2 x 33kV busbar disconnector switches connected off the new double 33kV busbar at the Relevant Transmission Licensee’s 132 / 33kV substation within the extended Mybster compound
|  | SHETL-RI-007C |  | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars.
|  | SHETL-RI-031 |  | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster).
AFTON WIND FARM LIMITED | Afton | SPT-RI-007 | Afton | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction. | 30/06/2017
|  | SPT-RI-115 | Afton | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill substation heading east to 132kV Black Hill Substation. Black Hill substation will include three new 132kV circuit breakers (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 30/06/2017
|  | SPT-RI-116A | Afton | Construction of Black Hill 132.33kV Substation including two 132kV circuit breakers (double busbar), two 132/33kV 90MVA transformers and 33kV B switchboard (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 30/06/2017
|  | SPT-RI-114 | Afton | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV Meikle Hill Collector Substation, heading east to 132kV Dun Hill Substation. These works will be required in response to new generation connections in the vicinity of Dun Hill substation. | 30/06/2017
RES UK & Ireland Limited | Annabaglish | SPT-RI-213 | Glenluce 132/33kV | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 31/10/2023
|  | SPT-RI-186 | Glenluce 132/33kV | Installation of an overhead protection scheme at Kilmarnock South 400/275kV substation. | 31/10/2023
|  | Annabaglish item 1 | Glenluce 132/33kV | At Glenluce 132kV substation installation of two new 132kV line isolators on the GT1B and GT2B transformers and two transformer 33kV circuit breakers, to form a second 33kV switchboard (B Board). Installation of all associated 33kV cabling to connect the Grid T1B and T2B transformers to the 33kV circuit breakers. | 31/10/2023
|  | SPT-RI-154 | Glenluce 132/33kV | There are currently ~102MW contracted at Glenluce GSP and a further 34.5MW (Annabaglish WF) is expected to accept their offer to connect. The amount of generation has reached a level where the thermal rating of 132kV double circuit between Glenluce and Newton Stewart is exceeded (currently 86MVA, Summer) and these circuits are therefore required to be uprated and to ensure compliance with the NETS SQSS. The existing two 132kV circuits between Glenluce and Newton Stewart are on double circuit tower lines and 132kV underground sections (For the overhead line termination at Newton Stewart end). The entire circuit route consists of BT Route (22km), towards Newton Stewart. These overhead line circuits are single 175mm² ACSR with a pre-fault summer rating of 86MVA. The total length of the entire circuit is ~22km. It is proposed to reconductor the 132kV circuits with 200mm² Poplar AAAC conductor on the existing double circuit tower lines between Glenluce and Newton Stewart. The new circuit will provide the following circuit ratings: 124MVA (Summer), 134MVA (Autumn) and 140 (Winter) pre-fault. | 31/10/2023
|  | SPT-RI-223 | Glenluce 132/33kV | Reconductor the existing circuits between Glenlee and Newton Stewart with High Temperature Low Sag conductors. | 31/10/2023
|  | SPT-RI-221 | Glenluce 132/33kV | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | 31/10/2023
|  | Annabaglish item 2 | Glenluce 132/33kV | At Glenluce 132kV substation, installation of two new 132kV line insolators on the GT1B and GT2B transformers, associated 132kV cablings and associated equipment. | 31/10/2023
Aquind Limited | Aquind Interconnector | 31832-3 | Lovedean 400kV Substation | Thermal reinforcement to the South Coast | 01/10/2020
|  | 31671-2 | Lovedean 400kV Substation | Re-conductoring Fleet - Lovedean 1&2 circuits | 01/10/2020
|  | 30752 | Lovedean 400kV Substation | Build and install a South West Operational Tripping Scheme (OTS) | 01/10/2020
|  | 31671-1 | Lovedean 400kV Substation | Re-conductoring Bramley - Fleet 1&2 circuits | 01/10/2020
Infinergy Ltd | Ardtaraig Wind Farm | Ardtaraig Item 1 |  | At Dunoon 132/33kV Grid Supply Point substation, replace the existing 2 x 45MVA 132/33kV grid transformers with 2 x 90MVA 132/33kV transformers. Upgrade the two 33kV transformer incomer breakers (1T0 and 2T0) and the corresponding Isolators (1T7 and 2T7) to accommodate the additional capacity. Undertake upgrades to the existing transformer plinths and foundations to accommodate the larger transformers. Connect the new 33kV transformer incomer breakers/isolators via suitably rated 33kV cabling to the new 90MVA units. As a result of the requirement to upgrade the existing 2 x 45MVA grid transformers a termination fee will be payable in respect of the asset removed prior to the end of its economic life. | 31/10/2021
|  | SHETL-RI-098 |  | Dunoon GL1-GL2 OHL Circuit Reconductoring — Reconductor approximately 17km of double circuit overhead line between Dunoon substation and the SHET – SPT boundary. Both sides of the double circuit OHL (GL1 and GL2) is to be reconductored | 31/10/2021
|  | SPT-RI-220 |  | New generation at SHETL’s Dunoon 132kV substation necessitates an uprating of the 132kV shared circuit between Dunoon and the tee into the Sloy-Windyhill circuit. SPT’s portion of the circuit runs between tower CM01 and mid span between CM13/14. The circuit presently uses 125mm2 ACSR Tiger conductor. It is proposed that SPT uprate the double circuit to Poplar 200mm2 conductor from CM1 to CM12. It is assumed SHETL will uprate over the boundary span between CM14 and CM13, terminating at tower CM12 | 31/10/2021
Fyne Futures Limited | Auchadaduie Wind Farm | SHETL-RI-011 & SPT-RI-006 | Carradale 132/33kV Substation | Establish a new 132kV substation at Crossaig in Kintyre with reactive compensation equipment. Connect in the existing 132kV double circuit line to Port Ann with Quadrature Booster transformers in circuit at Crossaig. Rebuild and connect in the existing 132kV double circuit line to Carradale. Establish two 240MVA subsea cable circuits (or three 120MVA cable circuits) between the new substation at Crossaig and the existing 132kV busbar at Hunterston. | 31/03/2017
|  | SHETL-RI-084 | Carradale 132/33kV Substation | Upgrade the capacity of the 132kV double circuit OHL between Carradale and Crossaig to 334MVA summer pre-fault rating using Araucaria conductor operated at 85°C. | 31/03/2017
Vattenfall Wind Power Ltd | Aultmore Wind Farm |  | Aultmore 132/33kV | The relevant transmission licensee will connect downdropper conductors between tower 34 of the Keither/Macduff single 132kV line and the adjacent terminal wood pole on the new trident 132kV line to the windfarm. | 01/07/2018
|  |  | Aultmore 132/33kV | The relevant transmission licensee will also install or modify (as applicable) intertripping arrangements between the Keith substations, Macduff substation and the wind farm substations. | 01/07/2018
Scottish & Southern Electricity Power Distribution | Axminster | NGET-RI-30752 |  | Creation of a new South West Operational Tripping Scheme (OTS) at Taunton.
|  | NGET-RI-31671-1 |  | Re-conductor the Bramley - Fleet OHL circuits to increase capacity.
|  | NGET-RI-31671-2 |  | Re-conductor the Fleet - Lovedean OHL circuits to increase capacity.
|  | NGET-RI-33539 |  | Hot wiring of the Hinckley Point - Melksham 1 and 2 circuits to increase their thermal rating.
Innogy Renewables UK Ltd | Bad a Cheo Wind Farm | SHETL-RI-032B | Mybster 132/33kV | Reinforce the existing 132kV double circuit overhead line between Dounreay, Thurso and Mybster substation (UTN/UTS and part of TME/TMW) Via a new 275/132kV substation at Spittal.
|  | SHETL-RI-035 | Mybster 132/33kV | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs.
|  | SHETL-RI-036 | Mybster 132/33kV | Reconductor part of the first 275kV circuits (BT1 - Beauly - Kilbraur - Gordonbush - Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substation (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay.
|  | SHETL-RI-037 | Mybster 132/33kV | Establish a new 275/132kV Fyrish substation close to the existing Alness 132kV OHL Tee location. The substation shall interface with the 275kV double-circuit between Beauly and Loch Buidhe. An optimal 132kV route will be designed and engineered to link the new 275/132kV Fyrish substation with the existing Alness GSP.
|  | SHETL-RI-058 | Mybster 132/33kV | Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe (Cambusmore) 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include two new Super Grid Transformers to connect Shin 132kV substation, new double circuit steel lattice tower L3/1 construction approximately 40km and works Beauly and Loch Buidhe 275kV substations.
|  | SHETL-RI-060 | Mybster 132/33kV | Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay (LT1/TD1/DU1) making it the same specification as the east side (LY2/YU2).
|  | Bad A Cheo Part 1 | Mybster 132/33kV | Install 2 x 33kV busbar disconnector switches connected off the new double 33kV busbar at the relevant transmission licensee's 132/33kV substation with the extended Mybster compound.
|  | SHETL-RI-002 & SPT-RI-001A | Mybster 132/33kV | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation.
|  | SHETL-RI-038 | Mybster 132/33kV | Install an operational intertrip scheme on the Errochty - Tummel 132kV circuit breakers, at Errochty 132kV substation.
|  | SHETL-RI-032A | Mybster 132/33kV | A new 275kV overhead line and substation works between Dounreay, Thurso and Spittal Substations.
|  | SHETL-RI-007C | Mybster 132/33kV | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars.
|  | SHETL-RI-031 | Mybster 132/33kV | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster).
Baglan Generating Ltd & Baglan Operations Ltd | Baglan Bay | 20551 | Baglan Bay | 1. Thermal uprate of the Aberthaw – Tremorfa circuit 2. Thermal uprate of the circuits from Whitson – Iron Acton – Melksham 3. Thermal uprate of the Imperial Park – Melksham and the Cilfynydd – Whitson – Seabank circuit (Severn Cable circuits) 4. Thermal uprate of the Cowley – Walham circuit 5. Thermal uprate of the Cardiff East – Uskmouth – Whitson circuit 6. Thermal uprate of the Cardiff East leg of the Pyle – Aberthaw – Cardiff East circuit 7. Thermal uprate of the Uskmouth – Whitson 2 circuit 8. Thermal uprate of Whitson SGT5
Beatrice Offshore Windfarm Ltd | Beatrice Wind Farm | SHETL-RI-007C | Beatrice 33/132kV Offshore Substations | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | 01/04/2018
Peel (Yell) Wind Farms Limited | Beaw Field Wind Farm | SHETL-RI-053 | Yell | It is required to construct a 600MW HVDC link from Shetland to the Scottish mainland at an HVDC switching station in the vicinity of Sinclair's Bay in Caithness. The HVDC switching station works will integrate with the Caithness-Moray Transmission Reinforcement. The HVDC link includes a 600MW HVDC converter station and 132kV substation at Kergord in Shetland. The new 132kV substation at Kergord will be the collection point for the large volume of wind generation in Shetland. The 600MW HVDC link will have approximately 13km of land cable and 284km of Subsea cable between Shetland and the HVDC switching station in Caithness.
|  | SHETL-RI-062 | Yell | An HVDC switching station is required to integrate the Caithness - Moray transmission reinforcement and the Shetland connection. The HVDC switching station is proposed to be in the vicinity of Sinclair's Bay in Caithness. The HVDC switching station works will integrate with the Caithness - Moray transmission reinforcement and the Shetland HVDC link.
|  | Beaw Field item 1 | Yell | The connection will be provided by a transmission 132kV circuit from the new 132kV double busbar at Kergord substation. The 132kV circuit will consist of the following: (a) 20km of 132kV wood pole overhead line between Kergord and Mossbank on the northern shore of the main island. (b) 4km of 132kV subsea cabling between Mossbank (main island) and the Bay of Ulsta (on Yell). (c ) 6km of 132kV wood pole overhead line between the Bay of Ulsta and the Beaw Field wind farm development site on the isle of Yell. At the wind farm substation, the 132kV wood pole overhead line through Yell will terminate on a 132kV transformer circuit switcher 115 located at the wind farm 132/33kV substation compound. In addition, (i) install 2 x 132kV busbar selector disconnectors, along with associated busbar extensions and support structures within Kergord 132kV substation compound. (ii) Install 1 x 132kV line circuit breaker along with associated line disconnector at Kergord 132kV substation compound. (iii) Install 1 x 132kV transformer circuit switcher within the wind farm substation compound. (iv) Modify the existing protection and telecommunication equipment at Kergord 132kV substation to suit the new connection at Beaw Field.
|  | SHETL-RI-007C | Yell | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars.
|  | SHETL-RI-031 | Yell | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster).
ScottishPower Renewables (UK) Limited | Beinn an Tuirc 3 | Beinn An Tuirc III item 1 | Carradale 132/33kV Substation | At Carradale 132kV substation establish a new 1 x 132kV wind farm feeder circuit breaker (435) to be coupled to the RC2 circuit side of the existing 132kV Carradale - Crossaig double circuit tower line (RC1/RC2) within the existing Carradale 132/33kV Grid Supply Point substation compound. The 1 x 132kV circuit breaker shall be configured as a wind farm feeder unit and shall be coupled to the Beinn An Tuirc III wind farm overhead line circuit. Establish approx. 12km of new 132kV single circuit overhead wood pole trident circuit between Carradale 132kV substation compound and the Beinn An Tuirc III wind farm development. At Carradale the new overhead line circuit will be coupled to the new 1 x 132kV wind farm circuit breaker (435). At Beinn An Tuirc III the overhead line will terminate on to a new 132kV circuit switcher (115) to be installed within the Beinn An Tuirc III wind farm substation compound. The high voltage side of the wind farm substation transformer will be coupled to the new circuit switcher (115). Modify the existing protection and telecommunication schemes at Carradale and Crossaig substation to facilitate the connection of the new 132kV wind farm feeder circuit as required.
|  | SHETL-RI-013 | Carradale 132/33kV Substation | Establish a new 275/132kV Substation (Ardbrecknich) near the existing Inveraray/Taynuilt 132kV line route with two 360 MVA 275/132kV transformers. Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275kV double circuit OHL between Ardbrecknish and Dalmally Substations.
|  | SHETL-RI-050 | Carradale 132/33kV Substation | Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 84km of 132kV double circuit OHL steel lattice construction between Inveraray, Port An and Crossaig.
|  | SPT-RI-123 | Carradale 132/33kV Substation | Construction of Hunterston East 400kV Substation. These works are included as a part of the Western HVDC link project.
Blackcraig Wind Farm (Scotland) Limited | Blackcraig Wind Farm | SPT-RI-007 | Black Craig | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction.
|  |  | Black Craig | Installation of a 132kV line circuit breaker at Magree Substation and from this point construction of a 132kV single circuit overhead line Blackcraig wind farm terminating at a 132kV isolator at Blackcraig Wind farm site.
|  |  | Black Craig | Provision of equipment to receive communications, alarms, indications and metering.
|  | SPT-RI-111 | Black Craig | The Kendoon to Maybole T 132kV single circuit will be reconfigured to form two new circuits, a circuit from Kendoon to New Cumnock, and a circuit from New Cumnock to Margree windfarm substation.
RES UK & Ireland Limited | Blary Hill Wind Farm | SHETL-RI-011 & SPT-RI-006 | Carradale | Establish a new 132kV substation at Crossaig in Kintyre with reactive compensation equipment. Connect in the existing 132kV double circuit line to Port Ann with Quadrature Booster transformers in circuit at Crossaig. Rebuild and connect in the existing 132kV double circuit line to Carradale. Establish two 240MVA subsea cable circuits (or three 120MVA cable circuits) between the new substation at Crossaig and the existing 132kV busbar at Hunterston.
|  | SHETL-RI-084 | Carradale | Upgrade the capacity of the 132kV double circuit OHL between Carradale and Crossaig to 334MVA summer pre-fault rating using Araucaria conductor operated at 85°C.
|  | SHETL-RI-077 & SPT-RI-150 | Carradale | Establish a third 240MVA 220kV subsea cable circuit between Crossaig 132kV Substation and Hunterston 400kV Substation.
|  | NGET-RI-30203 & SPT-RI-123 | Carradale | These works are part of the West Coast HVDC project.
|  | Blary Hill item 5 | Carradale | At Carradale 132/33kV substation The Relevant Transmission Licensee shall replace the existing 2 x 60MVA 132/33kV transformers with higher rated 2 x 120MVA 132/33kV transformers within the same substation accommodation. The works include all associated plinth foundations, transformer protection equipment and cabling work associated with the installation of the replacement 120MVA 132/33kV Transformers. The incumbent 132kV circuit switchers and associated 132kV cabling are adequately rated to meet the capacity of the new 120MVA 132/33kV transformers. However the existing 33kV transformer circuit breakers and associated 33kV cabling is not and will need to be replaced in order to meet the capacity of the new transformers.
South Eastern Power Networks | Bolney |  |  | Thermal overload relief work.
|  | NGET-RI-11642 |  | Hotwiring of the Lovedean - Ninfield - Bolney circuits to increase their thermal rating.
|  | NGET-RI-21588 |  | Re-conductor the Dungeness - Sellindge OHL circuits to increase capacity.
|  | NGET-RI-30967 & NGET-RI-30968 |  | Construction of a new Sellindge double busbar bypass 400kV Substation.
|  | NGET-RI-31338, NGET-RI-31339 & NGET-RI-21497-5 |  | Installation of Flexible AC Transmission Solutions (FACTS) at Bolney, Ninfield and Richborough and associated works.
Scottish & Southern Electricity Power Distribution | Botley Wood | NGET-RI-30752 |  | Creation of a new South West Operational Tripping Scheme (OTS) at Taunton.
|  | NGET-RI-31671-1 |  | Re-conductor the Bramley - Fleet OHL circuits to increase capacity.
|  | NGET-RI-31671-2 |  | Re-conductor the Fleet - Lovedean OHL circuits to increase capacity.
Bradwell Power Generation Company Limited | Bradwell B | NGET-RI-20802-1 | Bradwell 400kV Substation | Installation of a new 4 bay 400kV AIS double busbar substation at Bradwell consisting of two Rayleigh main feeder bays, one skeletal generator bay, one bus coupler bay and of the system-to-generator intertrip.
|  | NGET-RI-20802-2 | Bradwell 400kV Substation | Extension of the Rayleigh main double busbar 400kV AIS section by 2 bays to facilitate two new Bradwell 400kV feeder bays.
|  | NGET-RI-20802-4 | Bradwell 400kV Substation | Rayleigh main overhead line route using new design of tower and new foundations and strung with 2 x 570mm² AAAC conductor operating at up to 90°C.
C.GEN Killingholme Ltd | C.Gen Killingholme North Power Station | NGET-RI-30544 | C.Gen North Killingholme | Extension of 400kV busbars and installation of bus section breakers and bus coupler for generation connections at the Western side of Killingholme 400kV Substation. | 01/04/2021
|  | NGET-RI-21406S | C.Gen North Killingholme | Extension of 400kV busbars and substation building and installation of series reactor for generation connections at Killingholme 400kV Substation. Extension to the existing South Humber Bank Operational Tripping Scheme | 01/04/2021
|  | NGET-RI-32278SI | C.Gen North Killingholme | Extend the busbar and a GIS skeletal bay and the associated foundation to provide 490MW CCGT connection. | 01/04/2021
South Eastern Power Networks | Canterbury North |  |  | Thermal overload relief work.
|  | NGET-RI-11642 |  | Hotwiring of the Lovedean - Ninfield - Bolney circuits to increase their thermal rating.
|  | NGET-RI-21588 |  | Re-conductor the Dungeness - Sellindge OHL circuits to increase capacity.
|  | NGET-RI-30967 & NGET-RI-30968 |  | Construction of a new Sellindge double busbar bypass 400kV Substation.
|  | NGET-RI-31338, NGET-RI-31339 & NGET-RI-21497-5 |  | Installation of Flexible AC Transmission Solutions (FACTS) at Bolney, Ninfield and Richborough and associated works.
Brims Tidal Array Limited | Cantick Head | SHETL-RI-002 & SPT-RI-001A | Bay of Skaill 132/33kV substation | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation.
|  | SHETL-RI-032A | Bay of Skaill 132/33kV substation | A new 275kV overhead line and substation works between Dounreay, Thurso and Spittal Substations.
|  |  | Bay of Skaill 132/33kV substation | The relevant transmission licensee will install a single 132kV circuit rated at a minimum of 180MVA, comprising approximately 10km of underground cable and 20km of subsea cable, between Cantick Head and South Ronaldsay 132kV substations. There will be two 132kV circuit switchers at Cantick Head substation and a fully equipped feeder bay at South Ronaldsay 132kV substation.
|  |  | Bay of Skaill 132/33kV substation | Reconfiguration of busbar at Mawwick Head substation to connect AC circuit to the section of the busbar with the HVDC link.
|  | SHETL-RI-005 | Bay of Skaill 132/33kV substation | Extend both the 275kV and 132kV busbars and install a second 275/132kV interbus auto-transformer at Dounreay substation. Upgrade the existing 150MVA interbus auto-transformer at Dounreay to 240MVA.
|  | SHETL-RI-006 | Bay of Skaill 132/33kV substation | Install two x 240MVA 220kV 3.6km underground cable circuits from a transition joint near Ardneil bay to Hunterston. Develop a new transformer compound at Hunterston comprising 2 x 400/220kV 240MVA transformers, each equipped with tertiary connected 60MVAr shunt reactors. Install two new feeder bays of 400kV GIS double busbar switchgear at Hunterston East 400kV Substation and establish 400kV connections to the new transformer compound. Complete Associated civil works and other miscellaneous works including installation/modification of associated protection, control, telecommunications and metering equipment.
|  | SHETL-RI-019 | Bay of Skaill 132/33kV substation | Establishment of a single 132kV AC circuit over a distance of approximately 70km between the proposed new 275kV GIS substation at Dounreay on the mainland and the new 132kV substation at the Bay of Skaill on Orkney. The 132kV circuit will comprise 9km of land cable and 91km of subsea cable element. Reactive compensation devices will be installed at both cable ends within the substation compounds at Dounreay and the Bay of Skaill. Two 33kV busbars complete with reactors will be installed and each connected to the 132kV busbars via two 120MVA 132/33kV GT's (four in total).
|  | SHETL-RI-020 | Bay of Skaill 132/33kV substation | Establish an HVDC link from Orkney to Peterhead in a phased manner to allow connection of marine and other renewable generation on and around the coast of Orkney. The works included in comprise an extension to the 132kV double busbar substation and a 600MW HVDC link from the northwest coast of Orkney to a HVDC switching station located inland in the vicinity of Sinclair’s Bay in Caithness. The HVDC link between Northwest Orkney and Sinclair’s Bay will have both land and subsea cable sections.
|  | SHETL-RI-021 | Bay of Skaill 132/33kV substation | Establish an HVDC link from Orkney to Peterhead in a phased manner to allow connection of marine and other renewable generation on and around the coast of Orkney. The works included in includes the 1200MW HVDC link to Peterhead and the HVDC switching station. The HVDC link between Northwest Orkney and Sinclair’s Bay will have both land and subsea cable sections.
|  | SHETL-RI-071 | Bay of Skaill 132/33kV substation | Establish 132kV transmission infrastructure between a new 132kV busbar on South Ronaldsay, Orkney and a new 132kV double busbar arrangement at Marwick Head on Orkney. The new 132kV infrastructure will be routed via Kirkwall to allow for provision of a new GSP near Kirkwall in the future.
|  | SHETL-RI-007C | Bay of Skaill 132/33kV substation | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars.
|  | SHETL-RI-031 | Bay of Skaill 132/33kV substation | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster).
Scottish & Southern Electricity Power Distribution | Chickerell | NGET-RI-30752 |  | Creation of a new South West Operational Tripping Scheme (OTS) at Taunton.
|  | NGET-RI-31671-1 |  | Re-conductor the Bramley - Fleet OHL circuits to increase capacity.
|  | NGET-RI-31671-2 |  | Re-conductor the Fleet - Lovedean OHL circuits to increase capacity.
|  | NGET-RI-33539 |  | Hot wiring of the Hinckley Point - Melksham 1 and 2 circuits to increase their thermal rating.
Chirmorie Wind Farm Limited | Chirmorie Wind Farm | SPT-RI-205 |  | Installation of approximately 1km of 132kV overhead line between Chirmorie Wind Farm substation and the tee point on the Mark Hill to Stranoch wind farm overhead line, a 132kV isolator at Chirmorie wind farm substation and 132kV substation at Mark Hill and a 132kV switch bay will be installed. From this a 132kV circuit consisting 0.5km of underground cable and 13.5 of 132kV overhead line 300mm UPAS conductor) will be installed to the overhead line tee point connecting the circuits to Chirmorie and Stranoch wind farms. | 31/10/2022
|  | SPT-RI-206 |  | At Mark Hill substation a 275kV switchbay will be installed to control a 275/132kV 240MVA transformer (SGT3). This will connect to a 132kV busbar (B Board) provided for the connection of renewable generation. | 31/10/2022
|  | SPT-RI-147 |  | A new 275kV double circuit overhead line will be constructed between Kilmarnock South and Coylton 275kV substation having a minimum summer pre-fault rating 1500MVA per circuit. In addition, the existing 132V circuit between Kilmarnock South and the Coylton T will be removed to facilitate a line routing for the third Kilmarnock South to Coylton 275kV circuit. Moreover, the Coylton 275/132kV SGT1 and SGT2 120MVA transformers will be replaced with 240MVA units to provide sufficient export capacity for the contracted generation in the area. | 31/10/2022
|  | SPT-RI-136 |  | Reconductor the 275kV single circuit overhead line (YY route) between Coylton 275kV substation and Mark Hill 275kV substation. | 31/10/2022
|  |  |  | Installation of approximately 1km of 132kV overhead line between Chirmorie wind farm substation and the tee point on the Mark Hill to Stranoch wind farm overhead line. | 31/10/2022
|  |  |  | Installation of a 132kV line isolator at Stranoch wind farm substation. | 31/10/2022
|  | SPT-RI-142 |  | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 31/10/2022
|  | SPT-RI-143 |  | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. | 31/10/2022
Vattenfall Wind Power Ltd | Clashindarroch 2 | SHETL-RI-072 | Cairnford | Replace the existing 55km XH1/XH2 275kV double circuit OHL with a 400kV double circuit OHL. The new 400kV OHL will terminate on the 400kV busbars at Blackhillock and Kintore substations.
|  | SHETL-RI-002 & SPT-RI-001A | Cairnford | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation.
|  | SHETL-RI-009 & SPT-RI-004 | Cairnford | Upgrade the Blackhillock/Kintore/Kincardine 400kV East coast route by upgrading the existing 275kV circuits to 400kV operation. Establish New 400kV busbars at Rothienorman, Kintore and Alyth to enable this upgrade. SPT own Kincardine substation and will be responsible for all 400kV conversion works at this location.
|  | SHETL-RI-004 | Cairnford | Reconductor the Beauly - Foyers - Blackhillock 275kV double circuit line with larger capacity conductor between Beauly - Knocknagael and between Knocknagael - Blackhillock and Blackhillock - Kintore (XH1/XH2). The substation at Knocknagael is adjacent to the existing Foyers line tee point.
|  | SHETL-RI-007C | Cairnford | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars.
Codling Wind Park Ltd | Codling Park Wind Farm | NGET-RI-31990L | Pentir Substation | Reconductor Taunton - Alverdiscott circuit with Triple Araucaria.
|  | NGET-RI-30106 | Pentir Substation | Reconductor the Trawsfynydd legs of the Deeside - Trawsfynydd - Legacy circuits with GAP conductor.
|  | NGET-RI-30308 | Pentir Substation | Install series compensation at Trawsfynydd 400kV Substation
|  | NGET-RI-30309 | Pentir Substation | Installation of series compensation in the Pentir - Trawsfynydd 1 and Pentir - Trawsfynydd 2 circuits.
|  | NGET-RI-30915 | Pentir Substation | Design, construct and commission a 2.5GW capacity VSC HVDC link from Wylfa to Pembroke comprising of a 2.5GW VSC based HVDC converter station local to the company's owned Wylfa 400kV substation in North Wales, a 2.5GW VSC based HVDC converter station local to the company's owned Pembroke 400kV substation in South Wales and a 2.5GW capacity HVDC linking the converter stations at Wylfa and Pembroke.
|  | NGET-RI-31813I | Pentir Substation | Extension of Pembroke 400kV substation building on both sides to accommodate two new GIS bays. Planning and consenting, if required, for the building extension. Double up of circuit breakers in 3 bus sections (X120, X220 and X320) and 2 bus coupler (X130 and X430) circuit breaker bays to satisfy loss of generation infeed requirement of the NETS SQSS. Extensions to Main bar 4 and Reserve bar 3/4 and main bar 1 and reserve bar 1/2 to extend the Pembroke 400kV busbar; provision and installation of two 400kV bay to facilitate the connection of Greenwire generation circuits. Replacement of all feeder circuit breakers and modification of feeder protections. Busbar protection replacement and substation control system modifications as required at Pembroke 400kV substation.
|  | NGET-RI-32014S1 | Pentir Substation | Install two new MSCDN's at Ironbridge 400kV substation.
|  | NGET-RI-32014S3 | Pentir Substation | Install two MSCDN's at Legacy 400kV.
|  | NGET-RI-32018 | Pentir Substation | Re-conductor the overhead line from Pentir - Deeside 400kV substation with Triple Araucaria.
|  | NGET-RI-32021 | Pentir Substation | Reconductor the Cellarhead - Drakelow 400kV circuit with 2 x 620mm² GZTACSR.
|  | NGET-RI-32022 | Pentir Substation | Increase the thermal capability of the existing South Manchester - Bredbury 275kV circuit.
|  | NGET-RI-32030 | Pentir Substation | Uprate the two Quad Boosters at Legacy to 2750MVA.
|  | NGET-RI-32056 | Pentir Substation | Establish one unpopulated skeletal generator bay in the Pentir 400kV GIS substation.
|  | NGET-RI-32029 | Pentir Substation | Reconductor the Legacy legs of the Deeside - Trawsfynydd - Legacy circuits with GAP conductor. Reconductor the Legacy - Shrewsbury - Ironbridge circuits with GAP conductor.
|  | NGET-RI-30311 | Pentir Substation | Stage 1 - Establish a second 400kV circuit between Pentir and Trawsfyndd comprising following elements a) Establishing a new 400kV 3 bay single switch mesh AIS substation at Penisarwaun. This substation will connect the Pentir – Dinorwig 2 - Trawsfynydd 400kV circuits; b) Installation of approximately 6 km of 2 cores per phase XLPE cable to cross the Glaslyn Estuary. c) Reconductor the existing sections of OHL between Penisarwaun and Trawsfynydd with 2 x 700mm2. d) Connect the circuit into the existing disconnector bay on Mesh Corner 3 at Trawsfynydd 400kV substation. e) Installation of a F3 ferroresonance quenching scheme on the SGT 3 Disconnector. Stage 2 - Increase the thermal capability of the existing Pentir - Trawsfynydd 400kV circuit.
|  | NGET-RI-32028 | Pentir Substation | Reconductor the Legacy - Shrewsbury - Ironbridge circuits with GAP conductor.
|  | NGET-RI-31829 | Pentir Substation | Establish a new 400kV GIS substation at Pentir 400kV
|  | NGET-RI-32014S2 | Pentir Substation | Install two MSCDN's at Connah's Quay.
SSE Generation Ltd | Coire Glas Pumped Storage |  | Coire Glas | Construction of approximately 10km of double circuit 400kV steel tower line and 2km 400kV cable from Invergarry to the connection site. | 31/10/2025
|  |  | Coire Glas | Installation of 400kV GIS double busbar arrangement and associated bus section circuit breakers/isolators at the connection site. | 31/10/2025
|  | SHETL-RI-068 | Coire Glas | Upgrade the existing 132kV double circuit OHL between Fort Augustus and Invergarry substation by a new 400kV OHL. The existing 132kV OHL forms part of the Fort Augustus to Fort William FFE/FFW circuits. Part of the upgrade is to establish a 400/132kV substation at Invergarry to connect the existing 132kV OHL from Fort William and Invergarry Generation. The new 400kV OHL will terminate into the 400kV busbar at For Augustus. | 31/10/2025
|  | SHETL-RI-069 | Coire Glas | A Static VAR Compensators (SVC) is required at Tummel Bridge for voltage support on the 275kV Beauly-Denny overhead line. The SVC will have a capability of +225MVAr and -75MVAr. Extend the 275kV busbar at Tummel bridge to accommodate the SVC. | 31/10/2025
|  | SHETL-RI-064 | Coire Glas | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | 31/10/2025
RockbySea Ltd | Coire Na Cloiche | SHETL-RI-035 | Alness GSP | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs. | 31/10/2018
|  | SHETL-RI-036 | Alness GSP | Reconductor part of the first 275kV circuits (BT1 - Beauly - Kilbraur - Gordonbush - Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substation (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay. | 31/10/2018
|  | SHETL-RI-037 | Alness GSP | Establish a new 275/132kV Fyrish substation close to the existing Alness 132kV OHL Tee location. The substation shall interface with the 275kV double-circuit between Beauly and Loch Buidhe. An optimal 132kV route will be designed and engineered to link the new 275/132kV Fyrish substation with the existing Alness GSP. | 31/10/2018
|  | SHETL-RI-007C | Alness GSP | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | 31/10/2018
|  | SHETL-RI-031 | Alness GSP | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). | 31/10/2018
Partnerships for Renewables Development | Craig II Wind Farm | SPT-RI-141 | Chapelcross 132/33kV Substation | The South West area of Scotland is an area rich in renewable energy resources such as onshore wind, offshore wind, hydro and marine. The network is primarily a legacy 132kV active and interconnected system which, along with the 275kV Auchencrosh circuit, is fully committed in terms of generation connections. It is proposed to establish a new 275kV supergrid infrastructure with a reduced 132kV radal network operating as local collector and supply hubs. The aim will be to extend the 275kV network from Harker to Auchencrosh to provide much needed additional capacity to the area for the connection of renewable generation.
|  | SPT-RI-161 | Chapelcross 132/33kV Substation | Installation of an Energy Management (Overload Protection) Scheme at Chapelcross 132kV substation. The scheme will issue a signal to SPD and/or SPT to disconnect the appropriate generators if the pre-fault continuous rating of any of the following circuits is exceeded: Chapelcross to Harker 132kV circuit, Chapelcross to Gretna No1 132kV circuit and Chapelcross to Gretna No2 132kV circuit.
|  | SPT-RI-168 | Chapelcross 132/33kV Substation | Installation of a protection scheme at Gretna 400/132kV substation. The scheme will issue a signal to the Host Distribution Network Operator to disconnect the appropriate generators if either SGT1 or SGT2 is overloaded or if both transformers are out of service (Following planned or unplanned outages).
|  | SPT-RI-208 | Chapelcross 132/33kV Substation | An overload protection scheme will be installed at Chapelcross 132/33kV substation. The scheme will issue a trip signal to Host Distribution Network Operator to disconnect the appropriate generators if Grid T1 or Grid T2 is overloaded.
Creag Riabhach Wind Farm Ltd | Creag Riabhach Wind Farm | SHETL-RI-035 | Creag Riabhach 132/33kV Substation | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs.
|  | SHETL-RI-036 | Creag Riabhach 132/33kV Substation | Reconductor part of the first 275kV circuits (BT1 - Beauly - Kilbraur - Gordonbush - Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substation (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay.
|  | SHETL-RI-052 | Creag Riabhach 132/33kV Substation | Establish a new 132kV double busbar arrangement at Lairg and build approximately 20km of new double circuit 132kV overhead tower line between Lairg and Loch Buidhe. It is expected that the first 10.5km of the new double circuit 132kV between Lairg and Loch Buidhe will be along the route of the existing Lairg - Shin (CS) 132kV OHL. A new route will have to be established for the remaining 9.5km (approx.) double circuit 132kV OHL.
|  | Creag Riabhach item 1 | Creag Riabhach 132/33kV Substation | Install 18km of single circuit 132kV overhead wood pole trident line, strung with conductors to match the capacity of the wind farm, between Dalchork 132/33kV grid substation and the location of the User’s 132/33kV substation on site of the proposed wind farm. At the wind farm site install a new 132kV line disconnector and earth switch.
|  | Creag Riabhach Item 2 | Creag Riabhach 132/33kV Substation | Connect the new 132kV overhead circuit from Dalchork 132/33kV grid substation to the Relevant Transmission Licensee’s 132kV metering circuit breaker installed within the User’s 132/33kV substation on site of the proposed wind farm.
|  | Creag Riabhach Item | Creag Riabhach 132/33kV Substation | At the new Dalchork 132/33kV grid substation install a new 132kV windfarm circuit breaker feeder bay complete with 2 x 132kV busbar selection switches, 1 x 132kV line disconnector and associated protection equipment.
|  | SHETL-RI-032A | Creag Riabhach 132/33kV Substation | A new 275kV overhead line and substation works between Dounreay, Thurso and Spittal Substations.
|  | SHETL-RI-007C | Creag Riabhach 132/33kV Substation | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars.
|  | SHETL-RI-031 | Creag Riabhach 132/33kV Substation | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster).
Crookedstane Windfarm Limited | Crookedstane Windfarm | None identified at this time | Crookedstane Windfarm Substation |  | 30/10/2017
Crossdykes Wind Farm Limited | Crossdykes | SPT-RI-017 | Crossdykes 33kV Substation | Construction of a single circuit 132kV overhead line (15km) and single cable circuits (1km) from Gretna substation, heading north, to a wind farm site. These works will be required in response to new generation connections in the vicinity of Gretna. | 31/10/2018
|  | SPT-RI-189 | Crossdykes 33kV Substation | A 132/33kV substation will be established adjacent to Ewe Hill Wind Farm, in Dumfries and Galloway. The substation will be connected to a new 132kV circuit from Gretna 400/132kV substation. It will provide a local 33kV point of connection for renewable generation from Ewe Hill and Crossdykes wind farms. This TORI describes the works required for the installation of a 90MVA, 132/33kV transformer at Ewe Hill Farm. | 31/10/2018
Cumberhead Wind Energy Limited | Cumberhead | Cumberhead Item 1 | Cumberhead | Establish a 132kV substation at the Cumberhead Wind Farm site. | 20/10/2019
|  | Cumberhead Item 2 | Cumberhead | Installation of a 132kV line disconnector and 132kV busbar. | 20/10/2019
|  | Cumberhead Item 3 | Cumberhead | Install 0.4km of 1600mm2 Al XLPE cable to loop in to the Coalburn – Galawhistle Collector substation circuit. | 20/10/2019
|  | SPT-RI-144 | Cumberhead | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 20/10/2019
|  | Cumberhead Item 4 | Cumberhead | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | 20/10/2019
|  | SPT-RI-180 | Cumberhead | Coalburn SGTx Overload Protection Scheme: An overload protection scheme will be installed at Coalburn 400/132kV substation such that if SGT1 or SGT2 is overloaded, a trip signal will be issued to SPD at Linnmill GSP, and/or to SPT generation connected directly to Coalburn 132kV substation, to disconnect the appropriate generators to remove the overload. Following completion of Coalburn SGT3 (SPT-RI-144), this transformer will be added to the overload scheme proposed in this TORI (SPT-RI-180). | 20/10/2019
Forewind Ltd | Dogger Bank Platform 1 | NGET-RI-31569 | Dogger Bank 220/33kV Offshore Substations | Extend Creyke Beck 400kV Substation to make available a single skeletal generator bay for the Relevant Transmission Licensee at the Interface, assuming a single offshore transmission circuit. | 01/04/2021
Dorenell Windfarm Limited | Dorenell Wind Farm | Dorenell Wind Farm Part 1 | Dorenell 132/33kV | Part 1 – Enabling Works 1. Installation of 2 x 132kV Transformer circuit switchers and associated 132kV busbars at the new Dorenell 132/33kV substation. 2. Installation of 2 x 23km of 132kV overhead composite pole line between Dorenell wind farm132/33kV substation and the future upgraded Blackhillock 400/275/132kV substation. Each circuit shall be constructed using 300 sqmm UPAS conductor, with a conductor operating temperature of 75°C, to provide a minimum summer pre-fault rating of 176MVA. 3. At the future upgraded Blackhillock 400/275/132kV substation, install two 132kV feeder circuit breaker bays (for the two 132kV line circuits from Dorenell), complete with 2 x 132kV busbar disconnector switches, 1 x line disconnector, and associated 132kV protections on each bay. 4. Connect the new 2 x 132kV overhead line circuits from the Dorenell windFarm 132/33kV substation to the Relevant Transmission Licensee’s new 132kV circuit breaker bays at Blackhillock 400/275/132kV substation. | 01/04/2018
|  | SHETL-RI-007C | Dorenell 132/33kV | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | 01/04/2018
3R Energy Solutions | Douglas West | SPT-RI-155 | Coalburn132/33kV | Replace the 3.2km 132kV undergroud cable section on the Coalburn to Linmill No.1 132kV circuit. | 31/10/2021
|  | SPT-RI-144 | Coalburn132/33kV | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 31/10/2021
|  |  | Coalburn132/33kV | Establish a 132kV substation at the Coalburn North 132kV substation. | 31/10/2021
|  |  | Coalburn132/33kV | Install a 132kV line disconnector and 132kV busbar. | 31/10/2021
|  |  | Coalburn132/33kV | Install 0.1km of 2000mm² Cu XLPE cable to loop in to the cable section of the Coalburn - Linnmill No.1 132kV circuit. | 31/10/2021
|  | NGET-RI-11629 | Coalburn132/33kV | Reconductor the Norwich - Walpole route (4VV) with 3 x 700mm² AAAC conductor operating at 75°C. | 31/10/2021
|  | NGET-RI-21071-1L | Coalburn132/33kV | Loop into the new Kings Lynn B 400kV substation to form a Walpole. The new 2.7km double circuit 400kV OHL route to Kings Lynn B Power Station rated to match that of the Walpole - Norwich route following the re-conductoring, namely 3x 700mm2 AAAC conductor sagged to a 75°C operating profile. | 31/10/2021
|  | NGET-RI-30145L | Coalburn132/33kV | Double tee the Norwich - Walpole double circuit into the new Necton 400kV substation to form the Norwich - Necton - Walpole 1 and 2 circuits. | 31/10/2021
|  | NGET-RI-30145S | Coalburn132/33kV | Construction of a five bay 400kV AIS substation at Necton including two feeder bays, one coupler bay and two skeleton OFTO bays. Installation of a system - generator intertrip. | 31/10/2021
|  | NGET-RI-30145S1 | Coalburn132/33kV | Install an additional circuit breaker at Norwich Main on the current Walpole - Norwich 1 circuit to remove the circuit complexity restriction and allow the tee in at the new Necton 400kV substation. | 31/10/2021
|  | NGET-TI-30145LC | Coalburn132/33kV | OHL modification to accommodate new circuit breaker at Norwich main. | 31/10/2021
Druim Leathann Windfarm Ltd | Druim Leathann | SHETL-RI-007B | Druim Leathann 132/33kV substation | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | 31/12/2020
|  | SHETL-RI-042 | Druim Leathann 132/33kV substation | Western Isles HVDC Link — Establish a 600MW HVDC link with associated equipment and converter stations between the Western Isles (Arnish on Lewis) and the 400kV double busbar at Beauly (SHETL-RI-007b). The HVDC cable to be routed approximately 79km subsea cable, and approximately 80km by land cable. The HVDC infrastructure interface with a new 132kV double busbar at Arnish (Lewis) and the 400kV double busbar at Beauly. | 31/12/2020
|  | Druim leathann Item 1 | Druim Leathann 132/33kV substation | Installation of a single circuit 24km wood pole overhead circuit between the Druim Leathann windfarm and the proposed 132kV substation at Arnish, with one 132kV circuit switcher at Druim Leathann windfarm and a fully equipped 132kV feeder bay at Arnish 132kVsubstation. | 31/12/2020
Viridor Enviroscot Limited | Dunbar ERF |  | Dunbar | Establishment and installation of two 132kV line isolators at Dunbar GSP. | 31/10/2021
|  | SPT-RI-137 | Dunbar | Currently there is ~161MW contracted at Dunbar Grid Supply Point. In order to provide firm capacity for the generations, it is proposed to reinforce the Torness/Innerwick/Dunbar No.1 and No 2 132kV circuits, consisting of tower lines and underground cables to provide a minimum pre-fault summer rating of 160MVA per circuit. For the overhead line section, it is anticipated that the existing towers are not suitable for reconductoring to achieve the proposed rating hence a rebuilding of the tower lines is required. It is also proposed to reinforce the existing 132kV busbars/isolators at Innerwick 132kV substation to accommodate the minimum rating of 160MVA of the reinforced circuits. | 31/10/2021
ScottishPower Renewables (UK) Limited | East Anglia 2 | 20834-2 | Platform EA2A and Platform EA2B 220/33kV Offshore Substations | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design.
|  | 20834-2A | Platform EA2A and Platform EA2B 220/33kV Offshore Substations | Establish a new fully equipped GIS bay at Bramford 400kV substation interfacing with a 1200MW capacity OFTO circuit.
East Anglia THREE Limited | East Anglia 3 | 20834-2 | Platform EA3A and Platform EA3B 220/33kV Substations | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design.
|  | 20834-2A | Platform EA3A and Platform EA3B 220/33kV Substations | Establish a new fully equipped GIS bay at Bramford 400kV substation interfacing with a 1200MW capacity OFTO circuit.
|  | 20315L | Platform EA3A and Platform EA3B 220/33kV Substations | At Bramford 400kV substation carry out OHL and cable works to enable the turn in of the Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits.
|  | 20315S | Platform EA3A and Platform EA3B 220/33kV Substations | Construct an initial 9 bay 400kV GIS substation at Bramford as a 2 section substation with one bus coupler and two bus sections to be subsequently extended by a further section turning in existing Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits.
East Anglia FOUR Limited | East Anglia 4 | 20834-2 | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design. | 01/04/2027
|  | 20315L | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | At Bramford 400kV substation carry out OHL and cable works to enable the turn in of the Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits. | 01/04/2027
|  | 20315S | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | Construct an initial 9 bay 400kV GIS substation at Bramford as a 2 section substation with one bus coupler and two bus sections to be subsequently extended by a further section turning in existing Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits. | 01/04/2027
|  | 11630I | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | Reconductor the re-configured Norwich - Bramford (4YM route) with 3 x 700mm² AAAC conductor operating at 75°C. | 01/04/2027
|  | 20834-3 | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | Install two switchable series reactors on the Tilbury and Coryton South feeder circuits at Rayleigh main. | 01/04/2027
|  | 21847 | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | Building a new double circuit overhead line between the Bramford, Twinstead Tee and Pelham substation strung with 3x 700mm2 AAAC conductor at 750C (28km), connecting into the new Bramford 400kV GIS substation. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Twinstead Tee -Pelham double circuit and Bramford – Twinstead Tee – Braintree – Rayleigh Main double circuit. | 01/04/2027
|  | 30637-1 | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | Build a new five bay 400kV AIS double busbar substation in the Lowestoft area, including two skeleton generator feeder bays, two feeder bays ad a bus coupler and additional works to enable the connection of 800MW. | 01/04/2027
|  | 30637-2 | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | Tee in the Norwich to Bramford circuit to the new Lowestoft substation. | 01/04/2027
|  | 30641-1 | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | Cable sealing end work for the new OHL. | 01/04/2027
East Anglia FOUR Limited | East Anglia 5 | 20834-2 | Platform EA5A and Platform EA5B 220/33kV Substations | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design.
|  | 20834-3 | Platform EA5A and Platform EA5B 220/33kV Substations | Install two switchable series reactors on the Tilbury and Coryton South feeder circuits at Rayleigh main.
|  | 21847 | Platform EA5A and Platform EA5B 220/33kV Substations | Building a new double circuit overhead line between the Bramford, Twinstead Tee and Pelham substation strung with 3x 700mm2 AAAC conductor at 750C (28km), connecting into the new Bramford 400kV GIS substation. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Twinstead Tee -Pelham double circuit and Bramford – Twinstead Tee – Braintree – Rayleigh Main double circuit.
East Anglia FOUR Limited | East Anglia 6 | 30648-1 | Platform EA6A and Platform EA6B and Platform EA6C 220/33kV Substations | Establish two new feeder bays at Norwich 400kV substation for the connection of the new double circuit from Bacton. | 01/04/2025
|  | 32339LI | Platform EA6A and Platform EA6B and Platform EA6C 220/33kV Substations | Build a new double circuit from the new Bacton 400kV substation to the existing Norwich 400kV substation. | 01/04/2025
|  | 32339SI | Platform EA6A and Platform EA6B and Platform EA6C 220/33kV Substations | Build 400kV AIS double busbar substation in the Bacton area, including one skeleton generator bay, two feeder bays and a bus coupler and additional works to connect 600MW. | 01/04/2025
East Anglia One Limited | East Anglia One | 20834-2 | Platform EA One 220/66kV Offshore Substation | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design. | 03/01/2019
|  | 20834-2A | Platform EA One 220/66kV Offshore Substation | Establish a new fully equipped GIS bay at Bramford 400kV substation interfacing with a 1200MW capacity OFTO circuit. | 03/01/2019
East Anglia One Limited | East Anglia One North | 20834-2 |  | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design.
|  | 20834-2A |  | Establish a new fully equipped GIS bay at Bramford 400kV substation interfacing with a 1200MW capacity OFTO circuit.
Eastern Power Networks | Eaton Socon |  |  | Extend the existing Eaton Socon 400kV substation to provide for a new 400kV SGT3 bay and 400/132kV 240MVA transformer.
Elchies Wind Limited | Elchies Wind Farm | SHETL-RI-002 & SPT-RI-001A | Elchies 132/33kV Substation | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation.
|  |  | Elchies 132/33kV Substation | The establishment of a new 132/33kV substation compound at Elchies including all substation internal civil works, including plinth foundations, bases, access roadway and control/switchroom. The substation will be located approximately 7km north of Aberlour. The company reserves the right to revise this construction agreement and the relevant bilateral connection agreement upon advise from the relevant transmission licensee should the ground conditions require excessive and/or protracted civil works and additional infrastructure.
|  |  | Elchies 132/33kV Substation | Install a 7km 132kV wood pole trident line between Aberlour 275/132kV substation and the new 132/33kV substation facility at Elchie with the line terminated on the new 132kV switchgear installed at both substation ends. The 132kV wood pole line will be strung with 3 wire 175mm ACSR conductors, with a conductor operating temperature of 75°C, to meet the windfarm capacity.
|  |  | Elchies 132/33kV Substation | At Aberlour 275/132kV substation, install a 132kV feeder circuit breaker bay connected off the substation double 132kV busbars, complete with plinths/foundation, support structures, post insulators, busbars, line disconnector and associated protection, control and metering equipment.
|  |  | Elchies 132/33kV Substation | At the Elchies 132/33kV substation a new 132kV line disconnector and associated earth switch.
|  | SHETL-RI-079 | Elchies 132/33kV Substation | Reinforce the transmission network between Blackhillock and Aberlour (near Dufftown) by replacing part of the existing Glenfarcles - Keith (FK Circuit) 132kV OHL. It is proposed to replace the existing 132kV OHL with a new 275kV double circuit OHL.
|  | SHETL-RI-007C | Elchies 132/33kV Substation | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars.
ElecLink Ltd | ElecLink | NGET-RI-31832S | Sellindge 400KV Substation | The provision of one bus section bay and one bus coupler bay to facilitate the User connection at a new 400kV GIS 7 bay Sellindge substation.
E.ON Climate & Renewables UK Developments Limited | Enoch Hill | SPT-RI-007 | Enoch Hill 132/33kV | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction. | 30/11/2020
|  | SPT-RI-158 | Enoch Hill 132/33kV | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 30/11/2020
|  | SPT-RI-176 | Enoch Hill 132/33kV | 10. New Cumnock Overload Protection Scheme - To utilise the non-firm capacity at New Cumnock and the 132kV network in South West Scotland an overload protection scheme is required at New Cumnock substation to monitor the loading on the 275kV circuits from Coylton, supergrid transformers and 132kV circuits at New Cumnock to prevent any overloading on the transmission system. The scheme at New Cumnock will communicate with remote systems at Dunhill, Blackhill, Glenglass and Kendoon North substations to trigger tripping signals to generators connected at these substations. | 30/11/2020
|  | SPT-RI-186 | Enoch Hill 132/33kV | Installation of an overhead protection scheme at Kilmarnock South 400/275kV substation. | 30/11/2020
|  | Enoch Hill Part 1 | Enoch Hill 132/33kV | 1. Extend the new 132kV substation compound at New Cumnock collector substation site location Grid Reference E251966, N608134 and install 1 x 132kV feeder bay. 2. Establish new 132/33kV substation compound at Enoch Hill Wind Farm site location, Grid Reference E255430,N608980 including the control /switch room 3. Installation of 0.25km of 132kV underground cable between New Cumnock and Enoch Hill Wind Farm substation. 4. Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | 30/11/2020
|  | SPT-RI-162 | Enoch Hill 132/33kV | 9. Coylton 275kV Infrequent Infeed Loss Risk Protection - A protection scheme will be installed at Coylton 275kV substation, on the Ayr/Kilmarnock South No.1 and No.2 275kV circuits (XY Route), such that if a level of power flow from Coylton to Kilmarnock South is detected which may result in the Infrequent Infeed Loss Risk (as defined in the NETS Security and Quality of Supply Standard) being exceeded, a trip signal will be provided to the Relevant Transmission Licensee/or host Distribution Network Operator to disconnect generation as required such that the Infrequent Infeed Loss Risk is not exceeded. | 30/11/2020
|  | SPT-RI-142 | Enoch Hill 132/33kV | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/11/2020
|  | SPT-RI-143 | Enoch Hill 132/33kV | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. | 30/11/2020
FABLink Ltd | FAB Link Interconnector | 32311O | Exeter 400KV Substation | Move SVC 5 isolator/disconnectors and extend substation busbars to the West to provide a skeletal bay to connect the HVDC interconnector. | 01/12/2020
|  | 32311SI | Exeter 400KV Substation | Extend the substation busbar to the East to provide a skeletal bay to connect the HVDC interconnector. | 01/12/2020
Community Wind Power Ltd | Faw Side Community Wind Farm | Faw Side Item 4 | Faw Side Community Wind Farm | On V Route, install a junction tower to form a ‘T’ connection for the Faw Side Community Wind Farm 132kV circuit onto the Gretna to Hawick 132kv circuit. | 30/11/2024
|  | Faw Side Item 6 | Faw Side Community Wind Farm | Reinforce the Junction V to Harker 132kV circuit (from tower AL068 to Harker 132kV substation), to provide a minimum summer pre-fault continuous rating of 202MVA. | 30/11/2024
|  | SPT-RI-227 | Faw Side Community Wind Farm | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | 30/11/2024
|  | Faw Side Item 1 | Faw Side Community Wind Farm | Establish a 132kV substation compound at Faw Side Community Wind Farm site. | 30/11/2024
|  | Faw Side Item 5 | Faw Side Community Wind Farm | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of this Bilateral Connection Agreement | 30/11/2024
|  | SPT-RI-222 | Faw Side Community Wind Farm | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | 30/11/2024
|  | Faw Side Item 3 | Faw Side Community Wind Farm | Install approximately 2.6km of 132kV wood pole overhead line (with a minimum summer pre-fault continuous rating of 222MVA) from Faw Side Community Wind Farm substation, to the Gretna to Hawick 132kV tower line (V Route) | 30/11/2024
|  | SPT-RI-233 | Faw Side Community Wind Farm | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 30/11/2024
|  | SPT-RI-230 | Faw Side Community Wind Farm | It is proposed to reconductor approximately 36km of the 132kV overhead line existing Gretna to Hawick circuit (AL and V Route), between Gretna and the proposed Faw Side Community Wind Farm ‘T’ connection. It is proposed to utilise LARK HTLS conductor. NGET own a section of AL and V Route on this circuit and will have to reinforce to match the SPT proposals. | 30/11/2024
|  | Faw Side Item 2 | Faw Side Community Wind Farm | Install a 132kV line disconnector and 132kV busbar | 30/11/2024
Scottish & Southern Electricity Power Distribution | Fawley | NGET-RI-30752 |  | Creation of a new South West Operational Tripping Scheme (OTS) at Taunton.
|  | NGET-RI-31671-1 |  | Re-conductor the Bramley - Fleet OHL circuits to increase capacity.
|  | NGET-RI-31671-2 |  | Re-conductor the Fleet - Lovedean OHL circuits to increase capacity.
Seagreen Wind Energy Ltd | Firth of Forth Offshore Wind Farm 1A |  | Tealing 275/33kv | Extend the Tealing 275kV busbar to accommodate one feeder bay and one bus coupler. Upgrade the Tealing 275kV busbar to 4000A rating. Install 1 x 275kV fully equipped feeder bay, 1 x 275kV fully equipped bus coupler bay at Tealing 275kV substation and energy metering. | 30/06/2019
|  | NGET-RI-11642 | Tealing 275/33kv | Hotwiring of the Lovedean - Ninfield - Bolney circuits to increase their thermal rating. | 30/06/2019
|  | NGET-RI-21588 | Tealing 275/33kv | Re-conductor the Dungeness - Sellindge OHL circuits to increase capacity. | 30/06/2019
|  | NGET-RI-30967 & NGET-RI-30968 | Tealing 275/33kv | Construction of a new Sellindge double busbar bypass 400kV Substation. | 30/06/2019
|  | NGET-RI-31338, NGET-RI-31339 & NGET-RI-21497-5 | Tealing 275/33kv | Installation of Flexible AC Transmission Solutions (FACTS) at Bolney, Ninfield and Richborough and associated works. | 30/06/2019
|  | SPT-RI-124 | Tealing 275/33kv | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | 30/06/2019
Seagreen Wind Energy Ltd | Firth of Forth Offshore Wind Farm 1B |  | Tealing 275/33kv | Extend the Tealing 275kV busbar to accommodate one feeder bay and one bus coupler. Upgrade the Tealing 275kV busbar to 4000A rating. Install 1 x 275kV fully equipped feeder bay, 1 x 275kV fully equipped bus coupler bay at Tealing 275kV substation and energy metering. | 30/06/2019
Seagreen Wind Energy Ltd | Firth of Forth Offshore Wind Farm 2A East & 2A West |  |  | Completion of all associated protection and control works.
All associated miscellaneous and minor works, including provision of Category 2 intertripping scheme and Category 4 intertripping scheme, as defined in the Grid code.
Installation of 400kV plant and apparatus at Branxton 400kV substation which will form the connections to the two 2B East and 2B West transmission interface points, including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers.
|  | SPT-RI-124 |  | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system.
Seagreen Wind Energy Ltd | Firth of Forth Offshore Wind Farm 2B East & 2B West |  | Branxton 400kV | Completion of all associated protection and control works.
|  |  | Branxton 400kV | All associated miscellaneous and minor works, including provision of Category 2 intertripping scheme and Category 4 intertripping scheme, as defined in the Grid code.
|  |  | Branxton 400kV | Installation of 400kV plant and apparatus at Branxton 400kV substation which will form the connections to the two 2B East and 2B West transmission interface points, including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers.
|  | SPT-RI-130 | Branxton 400kV | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration.
|  | SPT-RI-131 | Branxton 400kV | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration.
|  | SPT-RI-124 | Branxton 400kV | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system.
Galloper Wind Farm Limited | Galloper Wind Farm | NGET-RI- 32490SI) | Galloper North 132/33kv | Supply and Install one GIS 132kV SGT bay, one AIS 400kV SGT bay and landing gantry for associated OHL tee connection works. Supply and Install two GIS 132kV skeletal bays, protection & control and associated civil works. Disconnection of Sizewell 132kV substation. | 01/01/2017
|  | NGET-RI- 32490LI | Galloper North 132/33kv | Replace existing set of cross-arms with modified set to allow tee-off into new sealing end compound. Install one set of down leads to gantries on Bramford - Sizewell 3 circuit, at tower 4ZX002. | 01/01/2017
|  | NGET-RI-32144 | Galloper North 132/33kv | Provision of a new system-generator operational intertripping system for East Anglia and associated extension to include Galloper Offshore Wind Farm. | 01/01/2017
Willowind Gass Limited | Gass Wind Farm |  | Newton Stewart | Installation of two new 132/33kV 90MVA transformer units (Grid T1 and T2) and all associated cablings to connect the transformers to Grid T1 and Grid T2 33kV circuit breakers on the Newton Stewart 33kV switchboard. | 30/10/2023
|  |  | Newton Stewart | Installation of one 132kV switchbay, three 1 line isolators and associated 132kV underground cables for interconnections and terminations at Newton Stewart 132kV substation. | 30/10/2023
|  | SPT-RI-141 | Newton Stewart | The South West area of Scotland is an area rich in renewable energy resources such as onshore wind, offshore wind, hydro and marine. The network is primarily a legacy 132kV active and interconnected system which, along with the 275kV Auchencrosh circuit, is fully committed in terms of generation connections. It is proposed to establish a new 275kV supergrid infrastructure with a reduced 132kV radal network operating as local collector and supply hubs. The aim will be to extend the 275kV network from Harker to Auchencrosh to provide much needed additional capacity to the area for the connection of renewable generation. | 30/10/2023
InterGen (UK) Ltd | Gateway Energy Centre Power Station | NGET-RI-21343-13 | Coryton South 400kV Substation | New bus coupler to be installed at Raleigh Main 400kV substation and re-distribution of the ZT circuits such that Bradwell - Rayleigh circuit 1 is re-distributed to the Rayleigh main busbar 1. Involves moving the Rayleigh Main - Coryton South circuit southwards to allow room to extend Rayleigh Main. This work will be conducted at the same time as that associated with works at Rayleigh associated with the connection of a new Rayleigh - Bradwell 400kV double circuit. | 30/09/2021
|  | NGET-RI-21343-15 | Coryton South 400kV Substation | Replace in situ existing OIBR bus section bay X120, bus coupler X130 and SGT1 and 4 bays X110, X410 respectively. | 30/09/2021
|  | NGET-RI-21343-23 | Coryton South 400kV Substation | Installation of necessary equipment to provide provision for a generator intertripping scheme at Coryton South 400kV to manage local outage/fault combinations on the circuits connecting the Coryton South - Tilbury - Grain or X205 (at Coryton South) & Rayleigh - Coryton South or X605 (at Rayleigh). | 30/09/2021
|  | NGET-RI-21850 | Coryton South 400kV Substation | Up-Rating of Rayleigh - Coryton South - Tilbury double circuit. | 30/09/2021
Gilston Hill Windfarm Limited | Gilston Hill Wind Farm | None identified at this time |  |  | 30/07/2023
Innogy Renewables UK Ltd | Glen Kyllachy Wind Farm | Glen Kyllachy Part 1 | Glen Kyllachy Wind Farm | Install a new 132 kV double busbar feeder bay comprising of 2 x132kV busbar selector disconnectors, 1 x 132kV line circuit breaker, 1 x 132kV line disconnector and associated protection and control equipment at Tomatin 275/132kV substation. The works also include establishment of a new 132kV single circuit connection between Tomatin 275/132kV substation and the Glen Kyllachy 132kV substation at the wind farm site. This will comprise of a 2.5km section of 132kV overhead wood pole trident line and a 0.5km section of underground 132kV cable circuit in order to facilitate entry into the proposed Tomatin 275/132kV substation compound. The new 132kV circuit will terminate into a new 132kV line disconnector installed at Glen Kyllachy 132kV substation. | 28/08/2019
|  | SHETL-RI-015a | Glen Kyllachy Wind Farm | Knocknagael – Tomatin 275/132kV Reinforcement - Reinforce the existing 132kV transmission network between Beauly–Farr–Boat of Garten (Circuits BR1/RG1/BR2/RG2). Note that the existing 132kV OHL passes close to Knocknagael substation. Establish a new 275/132kV substation station including a 132kV double busbar arrangement near Tomatin and connected to a new 275kV double circuit OHL from the Knocknagael 275kV busbar via 275/132kV SGTs. | 28/08/2019
Kilmac Energy | Glen Ullinish Wind Farm |  | Glen Ullinish 132/33kV Substation | Modify the tower near the new 132/33kV windfarm substation and erect a new terminal tower and down droppers to the new substation compound.
|  |  | Glen Ullinish 132/33kV Substation | Install 2 x 132kV line isolating switches (103 and 203) along with associated busbar extensions and support structures within the substation compound. Isolators to be located on either side of the single teed 132kV infeed to the substation.
|  |  | Glen Ullinish 132/33kV Substation | Install 1 x 132kV transformer circuit breaker (115) along with associated busbar extensions and support structures.
|  |  | Glen Ullinish 132/33kV Substation | Modify the existing protection and telecommunication equipment's at Fort Augustus and the new 132kV substation near Dunvegan.
|  | SHETL-RI-061 | Glen Ullinish 132/33kV Substation | Establish a new 132kV double busbar substation near Dunvegan on Skye and construct a new 132kV single circuit line Trident arrangement approximately 150km back to Fort Augustus 132kV busbar.
|  | SHETL-RI-002 & SPT-RI-001A | Glen Ullinish 132/33kV Substation | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation.
|  | SHETL-RI-064 | Glen Ullinish 132/33kV Substation | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers.
SSE Renewables Developments (UK) Ltd | Glencassley Wind Farm | SHETL-RI-035 | Shin 33kV | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs. | 31/10/2022
|  | SHETL-RI-036 | Shin 33kV | Reconductor part of the first 275kV circuits (BT1 - Beauly - Kilbraur - Gordonbush - Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substation (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay. | 31/10/2022
|  | SHETL-RI-052 | Shin 33kV | Establish a new 132kV double busbar arrangement at Lairg and build approximately 20km of new double circuit 132kV overhead tower line between Lairg and Loch Buidhe. It is expected that the first 10.5km of the new double circuit 132kV between Lairg and Loch Buidhe will be along the route of the existing Lairg - Shin (CS) 132kV OHL. A new route will have to be established for the remaining 9.5km (approx.) double circuit 132kV OHL. | 31/10/2022
|  | SHETL-RI-032A | Shin 33kV | A new 275kV overhead line and substation works between Dounreay, Thurso and Spittal Substations. | 31/10/2022
|  | SHETL-RI-007C | Shin 33kV | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | 31/10/2022
|  | SHETL-RI-031 | Shin 33kV | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). | 31/10/2022
RES UK & Ireland Limited | Glenchamber Wind Farm | SPT-RI-147 | Glenluce | A new 275kV double circuit overhead line will be constructed between Kilmarnock South and Coylton 275kV substation having a minimum summer pre-fault rating 1500MVA per circuit. In addition, the existing 132V circuit between Kilmarnock South and the Coylton T will be removed to facilitate a line routing for the third Kilmarnock South to Coylton 275kV circuit. Moreover, the Coylton 275/132kV SGT1 and SGT2 120MVA transformers will be replaced with 240MVA units to provide sufficient export capacity for the contracted generation in the area. | 30/04/2023
Glenmuckloch Pumped Storage Limite | Glenmuckloch Pumped Storage | Glenmuckloch Hydro Pumped Storage Item 3 | Glenmuckloch 132kV Substation | Install one new 132kV circuit breaker at New Cumnock Board B | 30/11/2022
|  | SPT-RI-213 | Glenmuckloch 132kV Substation | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 30/11/2022
|  | Glenmuckloch Hydro Pumped Storage Item 1 | Glenmuckloch 132kV Substation | Establish a 132kV substation at the Glenmuckloch Hydro Pumped Storage site | 30/11/2022
|  | SPT-RI-186 | Glenmuckloch 132kV Substation | Installation of an overhead protection scheme at Kilmarnock South 400/275kV substation. | 30/11/2022
|  | Glenmuckloch Hydro Pumped Storage Item 2 | Glenmuckloch 132kV Substation | Install ~22km of 132kV overhead line incorporating a fibre optic cable (POPLAR, wooden pole) from Glenmuckloch 132kV substation to New Cumnock 132kV substation Board B | 30/11/2022
|  | SPT-RI-142 | Glenmuckloch 132kV Substation | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/11/2022
|  | SPT-RI-143 | Glenmuckloch 132kV Substation | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. | 30/11/2022
Glenmuckloch Renewable Energy Limited | Glenmuckloch Wind Farm | SPT-RI-007 | Glenmuckloch 33kV | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction. | 30/08/2022
|  | SPT-RI-158 | Glenmuckloch 33kV | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 30/08/2022
|  | SPT-RI-114 | Glenmuckloch 33kV | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV Meikle Hill Collector Substation, heading east to 132kV Dun Hill Substation. These works will be required in response to new generation connections in the vicinity of Dun Hill substation. | 30/08/2022
|  | SPT-RI-115 | Glenmuckloch 33kV | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill substation heading east to 132kV Black Hill Substation. Black Hill substation will include three new 132kV circuit breakers (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 30/08/2022
|  | SPT-RI-142 | Glenmuckloch 33kV | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/08/2022
|  | SPT-RI-022 | Glenmuckloch 33kV | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | 30/08/2022
|  | SPT-RI-186 | Glenmuckloch 33kV | Installation of an overhead protection scheme at Kilmarnock South 400/275kV substation. | 30/08/2022
|  | SPT-RI-022 | Glenmuckloch 33kV | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | 30/08/2022
|  | SPT-RI-143 | Glenmuckloch 33kV | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. | 30/08/2022
Gamesa Energy UK Ltd | Glenouther Wind Farm (Harelaw) |  | Glenouther 132/33kV Substation | At Neilston 132kV substation, provide 132kV busbar connection, associated civil works and ancillary equipment | 30/05/2020
Simec Lochaber Hydropower 2 Limited | Glenshero | SHET-RI-069 | Glenshero | Tummel SVC – Installation of a Static VAR Compensator (SVC) at Tummel substation for voltage support on the 275kV Beauly-Denny overhead line. (SHET-RI-069) | 31/05/2022
|  | SHET-RI-085 | Glenshero | Melgarve 400/132kV Substation – Establish a new 400/132 kV Substation at Melgarve, to allow the connection of wind generation in the area. (SHET-RI-085) | 31/05/2022
E.ON Climate & Renewables UK Developments Limited | Golticlay Wind Farm | SHETL-RI-036 | Golticlay 132/33kV | Reconductor part of the first 275kV circuits (BT1 - Beauly - Kilbraur - Gordonbush - Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substation (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay. | 31/10/2022
|  | SHETL-Rl-060 | Golticlay 132/33kV | Loch Buidhe/Dounreay 275kv Circuit (DU1) Reconductoring | 31/10/2022
|  | SHETL-Rl-035 | Golticlay 132/33kV | Loch Buidhe 275/132kV New Substation - Construct a new 275/132kv substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kv and Shin-Mybster 1 32kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kv Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kv double busbar to the new 132kv double busbar via two 24OMVA 275/132kV SGTs. | 31/10/2022
|  | SHETL-Rl-032a | Golticlay 132/33kV | Dounreay Spittal 275kV & 132kV OHL Reinforcement - A new 275 kV overhead line and substation works between Dounreay,Thurso and Spittal Substations.( | 31/10/2022
|  | SHETL-Rl-007c | Golticlay 132/33kV | Blackhillock Substation Redevelopment - Redevelop Blackhillock Substation to enable the construction of a new 400kv, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 24GMVA 275/132kv SGTs. Connect the existing 2 x 24OMVA 275/132kv SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. | 31/10/2022
|  | SHETL-Rl-058 | Golticlay 132/33kV | Beauly-Loch Buidhe 275kV OHL Reinforcement (Rebuild) - This project is to reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe (Cambusmore) 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: (a). Two new Super Grid Transformers to connect Shin 132kV substation. (b). New double circuit steel lattice tower L3/1 construction approximately 40km. (c). Works at Beauly and Loch Buidhe 275kV substations. | 31/10/2022
|  | Golticlay Windfarm Part 1 | Golticlay 132/33kV | Establish a new 1 32kV Tee-off point on the future Loch Buidhe - Spittal 132kV double circuit OHL (currently known as MSW between Shin and Mybster), including any required tower modifications. Establish approximately 2.7km of new 132kV single circuit wood pole trident line between the new 132kV tee off point and Golticlay Wind Farm development. The 132kv wood pole trident circuit will terminate onto a new 132kV circuit switcher (115) to be installed within the Golticlay Wind Farm substation site compound. The 132kV circuit switcher (115) will be connected onto the high voltage terminals of the new 132/33kV Transformer unit. | 31/10/2022
|  | SHETL-RI-109 | Golticlay 132/33kV | Loch Buidhe — Spittal 132kv Reconductoring - Reconductor the existing 90km 132kV tower line between Loch Buidhe and Spittal substations. The 132kV overhead line is to be reconductored with a higher capacity conductor than the existing conductor, and should have a minimum summer pre4ault rating of 176MvA. | 31/10/2022
|  | SHETL-RI-031 | Golticlay 132/33kV | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). | 31/10/2022
SSE Generation Ltd | Gordonbush Wind | SHETL-RI-035 | Gordonbush | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs. | 31/10/2022
|  | SHETL-RI-036 | Gordonbush | Reconductor part of the first 275kV circuits (BT1 - Beauly - Kilbraur - Gordonbush - Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substation (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay. | 31/10/2022
|  | SHETL-RI-058 | Gordonbush | Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe (Cambusmore) 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include two new Super Grid Transformers to connect Shin 132kV substation, new double circuit steel lattice tower L3/1 construction approximately 40km and works Beauly and Loch Buidhe 275kV substations. | 31/10/2022
|  | SHETL-RI-060 | Gordonbush | Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay (LT1/TD1/DU1) making it the same specification as the east side (LY2/YU2). | 31/10/2022
|  | SHETL-RI-032A | Gordonbush | A new 275kV overhead line and substation works between Dounreay, Thurso and Spittal Substations. | 31/10/2022
|  | SHET-RI-106a | Gordonbush | Gordonbush Circuit Transfer - Transfer the connection of Gordonbush windfarm from the TD1 (West) 275kV circuit to the BNG2 (East) 275kV circuit to balance the power flows on the associated overhead line between Loch Buidhe and Dounreay. A new 275kV circuit breaker and line disconnectors are to be installed on the 275kV BNG2 (East) circuit, on the Connagill side of the new Gordonbush connection point. The existing line disconnectors will be dismantled and removed from the TD1 circuit. | 31/10/2022
|  | SHETL-RI-007C | Gordonbush | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | 31/10/2022
|  | SHETL-RI-031 | Gordonbush | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). | 31/10/2022
Lark Energy Limited | Greenford Farm Solar Farm | SHETL-RI-002 & SPT-RI-001A | Arbroath GSP | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 31/03/2016
Greenwire Transmission Pembroke Limited | Greenlink | NGET-RI-31813I | Pembroke 400kV Substation | Extension of Pembroke 400kV substation building on both sides to accommodate two new GIS bays. Planning and consenting, if required, for the building extension. Double up of circuit breakers in 3 bus sections (X120, X220 and X320) and 2 bus coupler (X130 and X430) circuit breaker bays to satisfy loss of generation infeed requirement of the NETS SQSS. Extensions to Main bar 4 and Reserve bar 3/4 and main bar 1 and reserve bar 1/2 to extend the Pembroke 400kV busbar; provision and installation of two 400kV bay to facilitate the connection of Greenwire generation circuits. Replacement of all feeder circuit breakers and modification of feeder protections. Busbar protection replacement and substation control system modifications as required at Pembroke 400kV substation.
|  | NGET-RI-20066IL | Pembroke 400kV Substation | Connect Swansea North - Cilfynydd circuit into the new 400kV substation creating the Cilfynydd - Rhigos and Swansea North - Rhigos 400kV circuits.
|  | NGET-RI-20066IS | Pembroke 400kV Substation | Construct new Rhigos 400kV 4-bay double substation, comprised of a bus coupler circuit breaker, two feeder circuit breakers, a skeletal generation bay, a new control system and all protection.
|  | NGET-RI-31843L | Pembroke 400kV Substation | Turn in of the Pembroke - Clifynydd and Pembroke - Walham 400kV circuits to Swansea North.
|  | NGET-RI-31843S | Pembroke 400kV Substation | Extend the existing GIS 400kV double busbar at Swansea North by installing of a new bus coupler bay, a circuit breaker in reserve bus section and addition of new bay to connect SGT4A.
Greenwire Transmission Pentir Limited | Greenwire Wind Farm - Pentir | NGET-RI-30106 | Pentir 400kV Substation | Reconductor the Trawsfynydd legs of the Deeside - Trawsfynydd - Legacy circuits with GAP conductor.
|  | NGET-RI-30308 | Pentir 400kV Substation | Install series compensation at Trawsfynydd 400kV Substation
|  | NGET-RI-30309 | Pentir 400kV Substation | Installation of series compensation in the Pentir - Trawsfynydd 1 and Pentir - Trawsfynydd 2 circuits.
|  | NGET-RI-31829 | Pentir 400kV Substation | Extend Pentir 400kV and establish one unpopulated skeletal AIS generator bay, including mitigation of SP Manweb owned 132kV circuits which traverse part of the extended substation site. Replace bus coupler circuit breaker X230 with two back-to-back circuit breakers.
|  | NGET-RI-32014S1 | Pentir 400kV Substation | Install two new MSCDN's at Ironbridge 400kV substation.
|  | NGET-RI-32014S3 | Pentir 400kV Substation | Install two MSCDN's at Legacy 400kV.
|  | NGET-RI-32018 | Pentir 400kV Substation | Re-conductor the overhead line from Pentir - Deeside 400kV substation with Triple Araucaria.
|  | NGET-RI-32021 | Pentir 400kV Substation | Reconductor the Cellarhead - Drakelow 400kV circuit with 2 x 620mm² GZTACSR.
|  | NGET-RI-32022 | Pentir 400kV Substation | Increase the thermal capability of the existing South Manchester - Bredbury 275kV circuit.
|  | NGET-RI-32030 | Pentir 400kV Substation | Uprate the two Quad Boosters at Legacy to 2750MVA.
|  | NGET-RI-32056 | Pentir 400kV Substation | Establish one unpopulated skeletal generator bay in the Pentir 400kV GIS substation.
|  | NGET-RI-32029 | Pentir 400kV Substation | Reconductor the Legacy legs of the Deeside - Trawsfynydd - Legacy circuits with GAP conductor. Reconductor the Legacy - Shrewsbury - Ironbridge circuits with GAP conductor.
|  | NGET-RI-30311 | Pentir 400kV Substation | Stage 1 - Establish a second 400kV circuit between Pentir and Trawsfyndd comprising following elements a) Establishing a new 400kV 3 bay single switch mesh AIS substation at Penisarwaun. This substation will connect the Pentir – Dinorwig 2 - Trawsfynydd 400kV circuits; b) Installation of approximately 6 km of 2 cores per phase XLPE cable to cross the Glaslyn Estuary. c) Reconductor the existing sections of OHL between Penisarwaun and Trawsfynydd with 2 x 700mm2. d) Connect the circuit into the existing disconnector bay on Mesh Corner 3 at Trawsfynydd 400kV substation. e) Installation of a F3 ferroresonance quenching scheme on the SGT 3 Disconnector. Stage 2 - Increase the thermal capability of the existing Pentir - Trawsfynydd 400kV circuit.
|  | NGET-RI-32014S2 | Pentir 400kV Substation | Install two MSCDN's at Connah's Quay.
|  | NGET-RI-32928 | Pentir 400kV Substation | Reconductor the Legacy - Shrewsbury - Ironbridge circuits with GAP conductor.
Gridlink Interconnector Ltd | Gridlink Interconnector | 33748 | Kingsnorth | Kinsnorth Works, including: - Provide the customer with a spare bay at Kingsnorth 400kV substation (spare bay 3). - Kingsnorth circuit breaker foundation (Xl 05, Xli 0, X140, X205, X21 0 X705 X805 and X1090) updating works - Installation of a new coupler breaker with associated bay works between main busbar 3 and circuit breaker X220. | 31/10/2022
ScottishPower Renewables (UK) Limited | Halsary Wind Farm | SHETL-RI-032B | Mybster 132/33kV Substation | Reinforce the existing 132kV double circuit overhead line between Dounreay, Thurso and Mybster substation (UTN/UTS and part of TME/TMW) Via a new 275/132kV substation at Spittal.
|  | SHETL-RI-007C | Mybster 132/33kV Substation | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars.
|  | SHETL-RI-031 | Mybster 132/33kV Substation | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster).
Innogy Renewables UK Ltd | Harryburn Wind Farm | Harryburn Wind Farm Part 1 | Elvanfoot 275/132/33kV | Installation of a 132kV disconnector. | 30/10/2020
|  | SPT-RI-226 | Elvanfoot 275/132/33kV | Installation of a new 275/132kV 360MVA transformer and a new 132kV busbar at Elvanfoot substation, to allow new generators to connect. | 30/10/2020
Banks Renewables (Harting Rig Wind Farm) Limited | Harting Rig Wind Farm | SPT-RI-144 | Harting Rig 132/33kv | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 30/07/2020
|  | SPT-RI-164 | Harting Rig 132/33kv | At Coalburn 400/132kV substation an additional 340MVA 400/132kV transformer (SGT4) will be installed. In addition a 400kV bus section circuit breaker will be installed on the Reserve busbar, and a second 400kV bus coupler circuit breaker will be installed on the Reserve busbar and a second 400kV bus coupler circuit breaker between the main and reserve busbars, along with a 400kV switchbay to connect SGT 5. The existing 132kV double busbar will be extended and split such SGT3 (Installed as part of TORI14) and SGT4 supply a separate section of 132kV double busbar (the B Board). On the B Board a 132kV feeder bay will be installed (for SGT4), a bus coupler 132kV circuit breaker and two 132kV switchbays (with associated 132kV cabling) to allow the transfer of two 132kV circuits from the A Board to the B Board as appropriate to the transformer capacity. This will increase the firm transformer capacity between the Coalburn 400kV and 132kV busbars to 600MVA (240MVA on Board A and 360MVA on Board B), to provide sufficient thermal capacity for the level of renewable generation contracted to connect o the Coalburn 132kV network. | 30/07/2020
|  |  | Harting Rig 132/33kv | Installation of one 132kV line isolator at Kype Muir Wind Farm substation. | 30/07/2020
|  | SPT-TI-181 | Harting Rig 132/33kv | Installation of one 132kV line isolator at Kype Muir Wind Farm Collector Substation. At Coalburn 132kV substation, install a 132kV circuit breaker disconnectors and associated apparatus to create the 132kV bay for the Kype Muir Wind Farm Collector Substation circuit. At Kype Muir Wind farm Collector Substation install a 132kV circuit breaker and associated apparatus to terminate the 132kV cable circuit from Coalburn Substation. | 30/07/2020
Sargas Power Yorkshire Limited | Hatfield Power Station | NGET-RI-20488L | Thorpe Marsh 400kV Substation | Install a new tower and line entries at Thorpe Marsh to connect the new substation in the Drax - Keadby - Brinsworth circuit. | 30/09/2022
|  | NGET-RI-20488S | Thorpe Marsh 400kV Substation | Construct a new 400kV AIS double busbar substation at Thrope Marsh of 2 feeder bays, 1 generator bay and 1 bus coupler bay, on the site of the decommissioned part of the 275kV substation, extended to the North and West onto land currently owned by RWE Generation UK plc. | 30/09/2022
EDF Energy Nuclear Generation Ltd | Hinkley Point C | NGET-RI-21132S | Hinkley 400kV Substation | Swaps the Hinkley Point – Melksham 2 circuit and the Bramley Melksham 2 circuit line entries at Melksham 400kV substation. | 01/06/2022
|  | NGET-RI-20832S | Hinkley 400kV Substation | Installation of a new 18-bay 400kV GIS double busbar substation at Hinkley Point, consisting of eight feeder bays, two bus couplers, four bus sections, two skeletal generator bays and two skeletal station transformer bays. | 01/06/2022
|  | NGET-RI-20898 | Hinkley 400kV Substation | Connecting new Hinkley Point - Seabank 1 circuit to the existing SGT4 bay. Tee-connect new Hinkley Point – Seabank 2 circuit to the existing Seabank – Melksham circuit at very close proximity to Seabank 400kV substation | 01/06/2022
|  | NGET-RI-21132L | Hinkley 400kV Substation | Construction of a short section of new OHL between the line entries of above two circuits at Melksham 400kv substation (approx 800m). | 01/06/2022
|  | NGET-RI-20832L | Hinkley 400kV Substation | Decommissioning the 2 Bridgwater feeder bays at Hinkley Point 275kV substation and re-configure all 6 of the existing 400kV and 275kV feeder circuits at Hinkley Point to facilitate a new connection between Hinkley point and Seabank. | 01/06/2022
|  | NGET-RI-20897L1 | Hinkley 400kV Substation | Breaking into the existing Hinkley Point - Melksham OHL route near M5 motorway and teeing it into the Hinkley Point - Bridgwater circuit by a short (4km) section of new OHL. Install 3 x 700mm² (Araucaria) or 2 x 850mm² (Redwood) conductors on the new build section of the OHL, operating at 90°C. | 01/06/2022
|  | NGET-RI-20897L2 | Hinkley 400kV Substation | Build a new circuit between the Hinkley Point leg of the broken Hinkley Point - Melksham OHL route and Seabank 400kV substation (~47km). Install 3 x 700mm² (Araucaria) or 2 x 850mm² (Redwood) conductors operating at 90°C. | 01/06/2022
|  | NGET-RI-21535S, NGET-RI-21535C & NGET-RI-21535T1, 21535T2 | Hinkley 400kV Substation | A new GSP at Sandford to supply WPD as a consequence of taking over WPD's 132kV 'F' route to construct the new Hinkley Point - Seabank OHL. | 01/06/2022
|  | NGET-RI-20897L4 | Hinkley 400kV Substation | Uprating the 275kV Hinkley Point - Bridgwater VQ route to 400kV operation and reconductoring from the tee point to Hinkley Point with GAP equivalent conductor. | 01/06/2022
|  | NGET-RI-20897Q | Hinkley 400kV Substation | The work associated with the removal of the existing fluid fill cables at Hinkley Point site between the terminal tower of the VQ route and the Hinkley Point A substation (275kV). | 01/06/2022
|  | NGET-RI-20899 & 20899C | Hinkley 400kV Substation | Replacing the 275kV disconnectors, earth switches, post insulators, CVTs and busbars at Bridgwater with 400kV equipment. Replacing the two 275/132kV SGTs at Bridgwater with two 400/275kV SGTs including associated protection. | 01/06/2022
Hirwaun Power Ltd | Hirwaun Power Station | NGET-32601SI | Rhigos | Extend the Rhigos 400kV substation busbar for the connection of Hirwaun Power Limited and one skeletal generator bay. Install two new feeder circuit bays for the turn-in of the Pembroke-Walham 400kV cable duck-under. Install one bus coupler bay. | 30/09/2020
|  | NGET-RI-20066IL | Rhigos | Connect Swansea North - Cilfynydd circuit into the new 400kV substation creating the Cilfynydd - Rhigos and Swansea North - Rhigos 400kV circuits. | 30/09/2020
|  | NGET-RI-20066IS | Rhigos | Construct new Rhigos 400kV 4-bay double substation, comprised of a bus coupler circuit breaker, two feeder circuit breakers, a skeletal generation bay, a new control system and all protection. | 30/09/2020
Hopsrig Wind Farm Limited | Hopsrig Wind Farm | Hopsrig Item 4 | Hopsrig Wind Farm 132/33kV Substation | Installation of a 132kV switchbay at Ewe Hill wind farm Collector Substation | 30/10/2021
|  | Hopsrig Item 3 | Hopsrig Wind Farm 132/33kV Substation | Installation of approximately 6.7km 132kV wood pole overhead line from Hopsrig wind farm to the Ewe Hill Collector Substation. | 30/10/2021
|  | Hopsrig Item 2 | Hopsrig Wind Farm 132/33kV Substation | Installation of one 1 32kV line Isolator at Hopsrig Wind Farm | 30/10/2021
|  | SPT-RI-017 | Hopsrig Wind Farm 132/33kV Substation | Construction of a single circuit 132kV overhead line (15km) and single cable circuits (1km) from Gretna substation, heading north, to a wind farm site. These works will be required in response to new generation connections in the vicinity of Gretna. | 30/10/2021
Heron Wind Ltd | Hornsea Power Station 1A | 21406S | Hornsea Platform 1A Offshore Substation | Extension of 400kV busbars and substation building and installation of series reactor for generation connections at Killingholme substation. Extension to the existing South Humber Bank Operational Tripping Scheme. | 30/09/2019
|  | 21406T1 | Hornsea Platform 1A Offshore Substation | Bulk purchase of the series reactor at Killingholme 400kV Substation. | 30/09/2019
|  | NGET-RI-30544 | Hornsea Platform 1A Offshore Substation | Extension of 400kV busbars and installation of bus section breakers and bus coupler for generation connections at the Western side of Killingholme 400kV Substation. | 30/09/2019
|  | 30544SI | Hornsea Platform 1A Offshore Substation | Extension of busbars at the Eastern end of Killingholme 400kV substation to accommodate a new OFTO bay for Hornsea P1. | 30/09/2019
Njord Ltd | Hornsea Power Station 1B | 21406S | Hornsea Platform 1B Offshore Substation | Extension of 400kV busbars and substation building and installation of series reactor for generation connections at Killingholme substation. Extension to the existing South Humber Bank Operational Tripping Scheme. | 28/02/2020
|  | 21406T1 | Hornsea Platform 1B Offshore Substation | Bulk purchase of the series reactor at Killingholme 400kV Substation. | 28/02/2020
|  | NGET-RI-30544 | Hornsea Platform 1B Offshore Substation | Extension of 400kV busbars and installation of bus section breakers and bus coupler for generation connections at the Western side of Killingholme 400kV Substation. | 28/02/2020
|  | 30544SI | Hornsea Platform 1B Offshore Substation | Extension of busbars at the Eastern end of Killingholme 400kV substation to accommodate a new OFTO bay for Hornsea P1. | 28/02/2020
Vi Aura Limited | Hornsea Power Station 1C | 21406S | Hornsea Platform 1C Offshore Substation | Extension of 400kV busbars and substation building and installation of series reactor for generation connections at Killingholme substation. Extension to the existing South Humber Bank Operational Tripping Scheme. | 01/07/2020
|  | 21406T1 | Hornsea Platform 1C Offshore Substation | Bulk purchase of the series reactor at Killingholme 400kV Substation. | 01/07/2020
|  | NGET-RI-30544 | Hornsea Platform 1C Offshore Substation | Extension of 400kV busbars and installation of bus section breakers and bus coupler for generation connections at the Western side of Killingholme 400kV Substation. | 01/07/2020
|  | 30544SI | Hornsea Platform 1C Offshore Substation | Extension of busbars at the Eastern end of Killingholme 400kV substation to accommodate a new OFTO bay for Hornsea P1. | 01/07/2020
Breesea Limited | Hornsea Power Station 2A | 21406S | Hornsea Platform 2A Offshore Substation | Extension of 400kV busbars and substation building and installation of series reactor for generation connections at Killingholme substation. Extension to the existing South Humber Bank Operational Tripping Scheme. | 01/10/2020
|  | 21406T1 | Hornsea Platform 2A Offshore Substation | Bulk purchase of the series reactor at Killingholme 400kV Substation. | 01/10/2020
|  | 31198 | Hornsea Platform 2A Offshore Substation | Extension of 400kV busbars and installation of bus section breakers and bus coupler for generation connections at the Western side of Killingholme 400kV Substation. | 01/10/2020
Breesea Limited | Hornsea Power Station 2B | 21406S | Hornsea Platform 2B Offshore Substation | Extension of 400kV busbars and substation building and installation of series reactor for generation connections at Killingholme substation. Extension to the existing South Humber Bank Operational Tripping Scheme. | 01/04/2021
|  | 21406T1 | Hornsea Platform 2B Offshore Substation | Bulk purchase of the series reactor at Killingholme 400kV Substation. | 01/04/2021
|  | 31198 | Hornsea Platform 2B Offshore Substation | Extension of 400kV busbars and installation of bus section breakers and bus coupler for generation connections at the Western side of Killingholme 400kV Substation. | 01/04/2021
Breesea Limited | Hornsea Power Station 2C | 21406T1 | Hornsea Power Station 2C Offshore platform | Bulk purchase of the series reactor at Killingholme 400kV Substation. | 01/10/2021
|  | 31198 | Hornsea Power Station 2C Offshore platform | Extension of 400kV busbars and installation of bus section breakers and bus coupler for generation connections at the Western side of Killingholme 400kV Substation. | 01/10/2021
SMart Wind SPC5 Limited | Hornsea Power Station 3A | 32452 | Hornsea Platform 3A Offshore Substation | Extension of the existing Norwich Main 400 kV substation to accommodate the connection of 2 skeletal bays, a new busbar coupler circuit breaker bay and a new reserve busbar section circuit breaker bay. Extension of the existing East Anglia Operational Tripping Scheme in accordance with Appendix F3 of the Bilateral Connection Agreement. | 01/04/2023
|  | 11630I | Hornsea Platform 3A Offshore Substation | Reconductor the re-configured Norwich - Bramford (4YM route) with 3 x 700mm² AAAC conductor operating at 75°C. | 01/04/2023
SMart Wind SPC6 Limited | Hornsea Power Station 3B | 32452 | Hornsea Platform 3B Offshore Substation | Extension of the existing Norwich Main 400 kV substation to accommodate the connection of 2 skeletal bays, a new busbar coupler circuit breaker bay and a new reserve busbar section circuit breaker bay. Extension of the existing East Anglia Operational Tripping Scheme in accordance with Appendix F3 of the Bilateral Connection Agreement. | 01/10/2023
|  | 11630I | Hornsea Platform 3B Offshore Substation | Reconductor the re-configured Norwich - Bramford (4YM route) with 3 x 700mm² AAAC conductor operating at 75°C. | 01/10/2023
SMart Wind SPC7 Limited | Hornsea Power Station 3C (Formally 4A) | 32452 | Hornsea Platform 3C Offshore Substation | Extension of the existing Norwich Main 400 kV substation to accommodate the connection of 2 skeletal bays, a new busbar coupler circuit breaker bay and a new reserve busbar section circuit breaker bay. Extension of the existing East Anglia Operational Tripping Scheme in accordance with Appendix F3 of the Bilateral Connection Agreement. | 01/04/2024
|  | 11630I | Hornsea Platform 3C Offshore Substation | Reconductor the re-configured Norwich - Bramford (4YM route) with 3 x 700mm² AAAC conductor operating at 75°C. | 01/04/2024
SMart Wind SPC8 Limited | Hornsea Power Station 3D (formally 4B) | 32452 | Hornsea Platform 3D Offshore Substation | Extension of the existing Norwich Main 400 kV substation to accommodate the connection of 2 skeletal bays, a new busbar coupler circuit breaker bay and a new reserve busbar section circuit breaker bay. Extension of the existing East Anglia Operational Tripping Scheme in accordance with Appendix F3 of the Bilateral Connection Agreement. | 01/10/2024
|  | 11630I | Hornsea Platform 3D Offshore Substation | Reconductor the re-configured Norwich - Bramford (4YM route) with 3 x 700mm² AAAC conductor operating at 75°C. | 01/10/2024
Hywind (Scotland) Ltd | Hywind Wind Farm | SHETL-RI-002 & SPT-RI-001A | Peterhead Grange | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 31/03/2017
National Grid International Ltd | IFA2 Interconnector |  | Chilling 400KV Substation | Build a new 400kV GIS double busbar substation. | 31/10/2019
|  |  | Chilling 400KV Substation | Install six new GIS Bays which are for four feeder circuits, one bus coupler and one shunt reactor. | 31/10/2019
|  |  | Chilling 400KV Substation | Provision for the User to install their GIS bay. | 31/10/2019
|  | NGET-RI-31671 | Chilling 400KV Substation | Turn in 400kV Fawley - Botley Wood/Lovedean circuits into it. Installing a shunt reactor on this site and connecting the User's 400kV AC cable from the User's converter station in this substation. | 31/10/2019
Inch Cape Offshore Ltd | Inch Cape Offshore Wind Farm Platform 1 |  | Cockenzie 275kV | Extend and uprate the Main and Reserve busbars at Cockenzie 275kV substation as required. | 01/04/2018
|  |  | Cockenzie 275kV | Install a new 275kV switchbay at Cockenzie 275kV substation and associated equipment and apparatus to the Interface point. | 01/04/2018
|  |  | Cockenzie 275kV | Provide communications, alarms, indications and metering. | 01/04/2018
Inch Cape Offshore Ltd | Inch Cape Offshore Wind Farm Platform 2 |  | Cockenzie 275kV | Extend and uprate the Main and Reserve busbars at Cockenzie 275kV substation as required. | 30/04/2020
|  |  | Cockenzie 275kV | Install a new 275kV switchbay at Cockenzie 275kV substation and associated equipment and apparatus to the Interface point. | 30/04/2020
|  |  | Cockenzie 275kV | Provide communications, alarms, indications and metering. | 30/04/2020
J G Pears Grid Connection Ltd | J G Pears | 33237I | High Marnham | Provision of the skeletal bay for the User to connect. The existing SGT1 skeletal bay assets are to be transferred to the User. | 08/04/2018
Keadby Generation Ltd | Keadby II | 31926S | Keadby | Scheme Description Extend main bar 2 and south side of reserve Bar 2 at Keadby 400kV substation to provide one skeleton bay at the busbar extension. Extend main bar 2 and south side of reserve Bar 2 at Keadby 400kV substation to provide one skeleton bay at the busbar extension. | 01/04/2021
Brookfield Renewable UK Ltd | Kennoxhead Wind Farm | SPT-RI-144 | Kennoxhead | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 31/10/2023
|  |  | Kennoxhead | New bay including one 132kV circuit breaker and all associated equipment and apparatus for the connection of the Kennoxhead wind farm circuit. | 31/10/2023
|  |  | Kennoxhead | Installation of approximately 0.3km 132kV underground cable and 17km of 132kV single circuit wooden pole overhead line with 200mm² conductor between Coalburn 132kV substation and Kennoxhead wind farm connection substation. | 31/10/2023
|  |  | Kennoxhead | Installation of one 132kV line isolator at Kennoxhead wind farm connection substation. | 31/10/2023
ScottishPower Renewables (UK) Limited | Kilgallioch |  | Kilgallioch 132/33kV Substation | Install a new 275kV switchbay at Mark Hill 275kV substation.
|  |  | Kilgallioch 132/33kV Substation | Establish a 275kV substation at the Kilgallioch wind farm site and install a 275kV line isolator and all the relevant transmission licensees protection/telecommunications apparatus required at the relevant transmission licensees Kilgallioch substation.
Kincardine Offshore Wind Limited | Kincardine Offshore Wind Farm | SHETL-RI-002 & SPT-RI-001A | Redmoss 132/33kV Grid Supply Point Substation | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 30/06/2018
EP UK Power Developments Limited | Kings Lynn B | NGET-RI-21071-1L | Kings Lynn B 400kV Substation | Loop into the new Kings Lynn B 400kV substation to form a Walpole. The new 2.7km double circuit 400kV OHL route to Kings Lynn B Power Station rated to match that of the Walpole - Norwich route following the re-conductoring, namely 3x 700mm2 AAAC conductor sagged to a 75°C operating profile. | 31/10/2021
|  | NGET-RI-11122 | Kings Lynn B 400kV Substation | Asset replacement of Walpole 132kV substation with a new GIS substation removing fault level restrictions currently precluding further 400kV and 132kV fault infeed at or near Walpole. | 31/10/2021
|  | NGET-RI-21071-1S | Kings Lynn B 400kV Substation | New 5 bay Kings Lynn B 400kV GIS substation and associated new LVAC protection and control works. This includes Current System generator intertripping scheme and New System generator intertripping facility. The scheme will also include extension of the existing East Anglia operational intertripping scheme. | 31/10/2021
Simec Lochaber Hydropower 2 Limited | Kinlochleven | SHETL-RI-002 & SPT-RI-001A | Kinlochleven | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 01/04/2022
|  | SHETL-RI-048 | Kinlochleven | Install a new fourth 240MVA 400/132kV SGT4 at Fort Augustus substation. Connect the new SGT to the existing 400kV OHL line Tee arrangement and 132kV double busbar. | 01/04/2022
|  | SHETL-RI-044 | Kinlochleven | Install a new 132kV OHL between Fort Augustus 132kV double busbar and SkyeTee. Connect the new 132kV OHL to a new 132kV circuit breakers at Fort Augustus. New 132kV Overhead line to be approximately 9km and to have a minimum rating equivalent to an ACSR lynx conductor at 50°C. Reinstate existing overhead line between Fort Augustus and Fort William. Modify any protection settings at Fort Augustus and Fort William for new arrangement. | 01/04/2022
|  | SHETL-RI-045 | Kinlochleven | Reconductor the 132kV double circuit OHL between Fort Augustus and Fort William (FFW/FFE). The 132kV double circuit OHL (FFE/FFE) is to be reconductored with a higher capacity conductor. This will have a minimum summer pre-fault rating of 130MVA per Circuit. Transfer the connection of Invergarry power station from FFE circuit of the OHL between Fort Augustus and Fort William to the FFW circuit. | 01/04/2022
Kirk Hill Wind Farm Limited | Kirk Hill | SPT-RI-147 | Maybole | A new 275kV double circuit overhead line will be constructed between Kilmarnock South and Coylton 275kV substation having a minimum summer pre-fault rating 1500MVA per circuit. In addition, the existing 132V circuit between Kilmarnock South and the Coylton T will be removed to facilitate a line routing for the third Kilmarnock South to Coylton 275kV circuit. Moreover, the Coylton 275/132kV SGT1 and SGT2 120MVA transformers will be replaced with 240MVA units to provide sufficient export capacity for the contracted generation in the area. | 30/09/2022
|  | SPT-RI-146 | Maybole | To accommodate the generation at Maybole GSP it is proposed to construct a new 132kV L7 double circuit tower line between Maybole and Coylton 132kV substations, with each circuit having a minimum summer pre-fault continuous rating of 150MVA. The existing 132kV overhead line circuits between Maybole and Coylton will be dismantled. | 30/09/2022
|  | SPT-RI-142 | Maybole | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/09/2022
|  | SPT-RI-143 | Maybole | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. | 30/09/2022
Knottingley Power Limited | Knottingley Power Station | 31868L | Knottingley | Single turn-in into the new Knottingley 400 kV substation the Eggborough – Ferrybridge to form an Eggborough – Knottingley and Ferrybridge – Knottingley circuit connection | 30/09/2019
|  | 31868S | Knottingley | Construct a new 5 bay Knottingley 400 kV GIS substation (two skeletal generator bays, two feeder bays and one bus coupler bay), associated new LVAC protection and control works. Installation of a local Operational Tripping Scheme in accordance with Appendix F3 of the Bilateral Connection Agreement | 30/09/2019
|  | 32906 | Knottingley | Circuit diversion at Eggborough 400 kV substation to connect together the Monk Fryston 1 and Drax 2 Circuits such that they no longer connect in to Eggborough 400 kV substation. Install an additional SGT at Monk Fryston 275kV substation and up rate the Drax - Monk Fryston circuit to match the new rating. | 30/09/2019
Banks Renewables Limited | Kype Muir | SPT-TI-181 | Coalburn 132/33kV | Installation of one 132kV line isolator at Kype Muir Wind Farm Collector Substation. At Coalburn 132kV substation, install a 132kV circuit breaker disconnectors and associated apparatus to create the 132kV bay for the Kype Muir Wind Farm Collector Substation circuit. At Kype Muir Wind farm Collector Substation install a 132kV circuit breaker and associated apparatus to terminate the 132kV cable circuit from Coalburn Substation. | 17/09/2018
|  |  | Coalburn 132/33kV | Installation of one 132kV line isolator at Kype Muir wind farm collector substation. | 17/09/2018
Infinergy Ltd | Limekilns | SHETL-RI-035 | Limekilns 132/33kV substation | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs.
|  | SHETL-RI-036 | Limekilns 132/33kV substation | Reconductor part of the first 275kV circuits (BT1 - Beauly - Kilbraur - Gordonbush - Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substation (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay.
|  | SHETL-RI-037 | Limekilns 132/33kV substation | Establish a new 275/132kV Fyrish substation close to the existing Alness 132kV OHL Tee location. The substation shall interface with the 275kV double-circuit between Beauly and Loch Buidhe. An optimal 132kV route will be designed and engineered to link the new 275/132kV Fyrish substation with the existing Alness GSP.
|  | SHETL-RI-058 | Limekilns 132/33kV substation | Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe (Cambusmore) 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include two new Super Grid Transformers to connect Shin 132kV substation, new double circuit steel lattice tower L3/1 construction approximately 40km and works Beauly and Loch Buidhe 275kV substations.
|  | SHETL-RI-060 | Limekilns 132/33kV substation | Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay (LT1/TD1/DU1) making it the same specification as the east side (LY2/YU2).
|  | SHETL-RI-002 & SPT-RI-001A | Limekilns 132/33kV substation | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation.
|  | Limekilns Item 10 | Limekilns 132/33kV substation | Erect standard 132kV busbars and connect the 132kV busbars with the newly established 275kV busbars with SuperGridTransformers (SGT), which provides 240MW firm capacity. Each SGT is equipped with a 132kV circuit breaker and a 275kV circuit switch. The 132kV busbars are planned with attention for the future expansion for generation connections.
|  | SHETL-RI-006 | Limekilns 132/33kV substation | Install two x 240MVA 220kV 3.6km underground cable circuits from a transition joint near Ardneil bay to Hunterston. Develop a new transformer compound at Hunterston comprising 2 x 400/220kV 240MVA transformers, each equipped with tertiary connected 60MVAr shunt reactors. Install two new feeder bays of 400kV GIS double busbar switchgear at Hunterston East 400kV Substation and establish 400kV connections to the new transformer compound. Complete Associated civil works and other miscellaneous works including installation/modification of associated protection, control, telecommunications and metering equipment.
|  | Limekilns Item 1 | Limekilns 132/33kV substation | Establishment of a new 132/33kV substation compound at Limekilns windfarm site including all substation internal civil works and the control/switchroom.
|  | Limekilns Item 2 | Limekilns 132/33kV substation | Construction of a wood pole 132kV trident line over a distance of 4km between Dounreay substation the new Limekilns 132/33kV substation. The line will be strung with 3 wire 150mm ACSR conductors and profiled to allow a 75°C conductor operating temperature, in order to meet the windfarm connection capacity. The 132kV line circuit will be terminated to new 132kV switchgear installed at the substation ends.
|  | Limekilns Item 3 | Limekilns 132/33kV substation | At Limekilns 132/33kV substation install a 132kV circuit breaker bay, complete with 132kV line disconnector and rated 132kV circuit breaker.
|  | Limekilns Item 4 | Limekilns 132/33kV substation | At Dounreay substation, install an additional 132kV circuit breaker on the indoor 132kV switchboard. These works will include the following: (i) Install 1 x 132kv line Gas Insulated switch- Disconnector (603) along with associated support structures within the substation compound. (ii) Install 1 x 132kv line Gas Insulated switch- Disconnector (605) along with associated support structures within the substation compound station. (iii) Modify the existing protection and telecommunication equipments at Dounreay 275/132 kV substation.
|  | Limekilns Item 9 | Limekilns 132/33kV substation | Identify, develop and construct a new 275kV/132kV substation north of Shin, along the existing MSE/W circuits erecting standard 275kV busbars within the compound. Connect the existing 275kV Beauly/Dounreay double circuits to the busbar, completed with circuit breakers.
|  | SHETL-RI-007C | Limekilns 132/33kV substation | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars.
Simec Lochaber Hydropower 2 Limited | Lochaber | SHETL-RI-002 & SPT-RI-001A | Fort William 33kV substation | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 31/10/2018
|  | SHETL-RI-044 | Fort William 33kV substation | Install a new 132kV OHL between Fort Augustus 132kV double busbar and SkyeTee. Connect the new 132kV OHL to a new 132kV circuit breakers at Fort Augustus. New 132kV Overhead line to be approximately 9km and to have a minimum rating equivalent to an ACSR lynx conductor at 50°C. Reinstate existing overhead line between Fort Augustus and Fort William. Modify any protection settings at Fort Augustus and Fort William for new arrangement. | 31/10/2018
Loganhead Wind Farm Limited | Loganhead Windfarm | SPT-RI-233 | EWE HILL WF 33/132KV COLLECTOR SUBSTATION | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | 31/10/2023
|  | SPT-RI-232 | EWE HILL WF 33/132KV COLLECTOR SUBSTATION | Ewe Hill Substation Transformer 132/33kV - Installation of a new 132/33kV 90MVA transformer at Ewe Hill Wind Farm Substation. This will create a new 33kV busbar to allow new generation to connect. (SPT-RI-232). | 31/10/2023
|  | NGET-RI-32105 | EWE HILL WF 33/132KV COLLECTOR SUBSTATION | Reconductor Harker – Gretna – Hawick circuit. Uprate the V route 132kV overload line circuit (between Tower V075 and Harker 132kV substation) to provide a minimum summer pre-fault continuous rating of 170MVA. (NGET-RI-32105) | 31/10/2023
Longburn Wind Farm Limited | Long Burn Wind Farm | SPT-RI-007 |  | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction.
|  | SPT-RI-213 |  | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B.
|  | SPT-RI-186 |  | Installation of an overhead protection scheme at Kilmarnock South 400/275kV substation.
|  | SPT-RI-111 |  | The Kendoon to Maybole T 132kV single circuit will be reconfigured to form two new circuits, a circuit from Kendoon to New Cumnock, and a circuit from New Cumnock to Margree windfarm substation.
|  | Longburn Item 1 |  | Install a 132kV overhead line (~2km) between Longburn Wind Farm substation and the junction with the overhead line from Lorg Wind Farm.
|  | SPT-RI-142 |  | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor.
|  | Longburn Item 2 |  | Establish a 132kV substation at the Longburn Wind Farm substation with a 132kV line isolator and all protection/telecommunications apparatus required for the Relevant transmission Licensee.
|  | SPT-RI-143 |  | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation.
E.ON Climate & Renewables UK Developments Limited | Lorg Wind Farm | SPT-RI-007 | Lorg Wind Farm 132/32kV | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction. | 15/11/2022
|  | Lorg Wind Farm PART 1 | Lorg Wind Farm 132/32kV | 1. Installation of 132kV overhead line (~8km) between Lorg Wind Farm and the junction with the overhead line from Longburn Wind Farm. 2. Installation of one disconnector at Lorg Wind Farm. | 15/11/2022
|  | SPT-RI-213 | Lorg Wind Farm 132/32kV | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | 15/11/2022
|  | SPT-RI-186 | Lorg Wind Farm 132/32kV | Installation of an overhead protection scheme at Kilmarnock South 400/275kV substation. | 15/11/2022
|  | SPT-RI-111 | Lorg Wind Farm 132/32kV | The Kendoon to Maybole T 132kV single circuit will be reconfigured to form two new circuits, a circuit from Kendoon to New Cumnock, and a circuit from New Cumnock to Margree windfarm substation. | 15/11/2022
|  | SPT-RI-142 | Lorg Wind Farm 132/32kV | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 15/11/2022
|  | SPT-RI-143 | Lorg Wind Farm 132/32kV | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. | 15/11/2022
Scottish & Southern Electricity Power Distribution | Lovedean | NGET-RI-30752 |  | Creation of a new South West Operational Tripping Scheme (OTS) at Taunton.
|  | NGET-RI-31671-1 |  | Re-conductor the Bramley - Fleet OHL circuits to increase capacity.
|  | NGET-RI-31671-2 |  | Re-conductor the Fleet - Lovedean OHL circuits to increase capacity.
Scottish & Southern Electricity Power Distribution | Mannington | NGET-RI-30752 |  | Creation of a new South West Operational Tripping Scheme (OTS) at Taunton.
|  | NGET-RI-31671-1 |  | Re-conductor the Bramley - Fleet OHL circuits to increase capacity.
|  | NGET-RI-31671-2 |  | Re-conductor the Fleet - Lovedean OHL circuits to increase capacity.
|  | NGET-RI-33539 |  | Hot wiring of the Hinckley Point - Melksham 1 and 2 circuits to increase their thermal rating.
Organic Power Ltd | Marex | NGET-RI-30915 | Connahs Quay 400kV | Design, construct and commission a 2.5GW capacity VSC HVDC link from Wylfa to Pembroke comprising of a 2.5GW VSC based HVDC converter station local to the company's owned Wylfa 400kV substation in North Wales, a 2.5GW VSC based HVDC converter station local to the company's owned Pembroke 400kV substation in South Wales and a 2.5GW capacity HVDC linking the converter stations at Wylfa and Pembroke.
|  | NGET-RI-32014S1 | Connahs Quay 400kV | Install two new MSCDN's at Ironbridge 400kV substation.
|  | NGET-RI-32014S3 | Connahs Quay 400kV | Install two MSCDN's at Legacy 400kV.
|  | NGET-RI-32021 | Connahs Quay 400kV | Reconductor the Cellarhead - Drakelow 400kV circuit with 2 x 620mm² GZTACSR.
|  | NGET-RI-32022 | Connahs Quay 400kV | Increase the thermal capability of the existing South Manchester - Bredbury 275kV circuit.
|  | NGET-RI-32030 | Connahs Quay 400kV | Uprate the two Quad Boosters at Legacy to 2750MVA.
|  | NGET-RI-32029 | Connahs Quay 400kV | Reconductor the Legacy legs of the Deeside - Trawsfynydd - Legacy circuits with GAP conductor. Reconductor the Legacy - Shrewsbury - Ironbridge circuits with GAP conductor.
|  | NGET-RI-32028 | Connahs Quay 400kV | Reconductor the Legacy - Shrewsbury - Ironbridge circuits with GAP conductor.
|  | NGET-RI-11076 | Connahs Quay 400kV | Reconductor Ironbridge - Rugely circuit with 2 x 570 AAAC conductors.
|  | NGET-RI-32014S2 | Connahs Quay 400kV | Install two MSCDN's at Connah's Quay.
|  | NGET-RI-32281 | Connahs Quay 400kV | Establish one unpopulated skeletal generator bay in the Pentir 400kV GIS substation.
|  | NGET-RI-32372LI | Connahs Quay 400kV | Increase thermal rating of Carrington - South Manchester circuit.
|  | NGET-RI-32373LI | Connahs Quay 400kV | Reconductor Connah's Quay - Daines circuit with London.
|  | NGET-RI-32374LI | Connahs Quay 400kV | Increase thermal rating of Cellarhead - Daines cable.
Margree Wind Energy Limited | Margree | SPT-RI-034 | Margree 132/33kV Substation | A 132/33kV substation will be established adjacent to Margree wind farm, near St Johns Town of Dalry, in Dumfries and Galloway. The substation will be connected to a new 132kV circuit from New Cumnock 275/132kV substation. It will provide a local 33kV point of connection for Margree wind farm (70.0MW), connection for a 33kV circuit to Loch Hill wind farm (27.5MW) and connection for 132kV circuit to Blackcraig wind farm (71.3MW).
|  | SPT-RI-111 | Margree 132/33kV Substation | The Kendoon to Maybole T 132kV single circuit will be reconfigured to form two new circuits, a circuit from Kendoon to New Cumnock, and a circuit from New Cumnock to Margree windfarm substation.
PNE Wind UK Ltd | Meikle Hill Wind Farm | SHETL-RI-002 & SPT-RI-001A | Elgin 275/132kV Substation | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 31/10/2020
|  | SHETL-RI-004 | Elgin 275/132kV Substation | Reconductor the Beauly - Foyers - Blackhillock 275kV double circuit line with larger capacity conductor between Beauly - Knocknagael and between Knocknagael - Blackhillock and Blackhillock - Kintore (XH1/XH2). The substation at Knocknagael is adjacent to the existing Foyers line tee point. | 31/10/2020
|  | SHETL-RI-007C | Elgin 275/132kV Substation | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | 31/10/2020
MeyGen Ltd | MeyGen Tidal | SHETL-RI-035 | Gills Bay | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs.
|  | SHETL-RI-036 | Gills Bay | Reconductor part of the first 275kV circuits (BT1 - Beauly - Kilbraur - Gordonbush - Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substation (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay.
|  | MeyGen Tidal Project item 1 | Gills Bay | Install a double circuit 132kV overhead line with a summer pre fault capacity of 348MVA between Thurso South and a new 132kV GIS double busbar arrangement within a new substation facility at Gills Bay connecting in the two OHL radial circuits from Thurso south.
|  | SHETL-RI-032A | Gills Bay | A new 275kV overhead line and substation works between Dounreay, Thurso and Spittal Substations.
|  | SHETL-RI-007C | Gills Bay | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars.
|  | SHETL-RI-031 | Gills Bay | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster).
Banks Renewables Limited | Middle Muir Wind Farm |  | Middle Muir 132/33kV | Installation of a new bay including one 132kV circuit breaker and all associated equipment apparatus at Coalburn 132kV substation for the connection of Middle Muir wind farm circuit. | 30/05/2018
|  |  | Middle Muir 132/33kV | Installation of one 132kV line isolator at Middle Muir wind farm connection substation. | 30/05/2018
|  | SPT-RI-144 | Middle Muir 132/33kV | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | 30/05/2018
Egnedol Pembroke Eco-Power Ltd | Milford Haven | 33793 |  | • Extension of Pembroke 400kV substation to accommodate one new GIS generator bay, including busbar protection and SCS update • Installation of a generator to system intertripping scheme (thermal and stability) • Replacement of feeder circuit breakers of Pembroke – Swansea North #1 and #3 and modification of feeder protection • Thermal uprate of the Whitson leg of Tremorfa - Uskmouth – Whitson circuit • Replacement of the Cowley – Walham cables • Thermal uprate of Imperial Park – Melksham and Cilfynydd – Whitson – Seabank circuits • Thermal uprate of the Iron Acton – Melksham circuits 1 and 2 • Thermal uprate of Iron Acton – Whitson circuits 1 and 2 • Remove the Quad boosters 1 and 2 at Whitson • Replacement of Whitson SGT5 for a larger rated unit • Thermal uprate of the Cardiff East – Uskmouth – Whitson (Cardiff East leg) • Thermal uprate of the Cardiff East – Uskmouth – Whitson (Whitson leg) • Thermal uprate of the Aberthaw – Tremorfa circuit. • Thermal uprate of the Cardiff East leg of the Pyle – Aberthaw – Cardiff East circuit | 31/10/2026
Falck Renewables Wind Ltd | Millennium South | Millennium South Item 1 | Millennium South 132/33kV Substation | 1. The enabling works associated with the new 132/33kV substation adjacent to structure 39 of the Fort Augustus – Skye 132kV trident wood pole line (FQ1) will include the following: a. Modify structure 39 of the Fort Augustus – Skye 132kV trident wood pole line (FQ1) and erect a new terminal tower and down droppers to the new substation compound; b. Install 2 x 132kV line disconnectors (103 and 203) along with associated support structures within the substation compound. Disconnectors 103 and 203 to be located on either side of the single teed 132kV infeed to the substation. c. Install 1 x 132kV transformer circuit switcher (115), along with support structures within the substation compound. d. Provide a double 132kV tapping from either side of structure 39 to two new wood pole terminal structures located adjacent to the tower, and then extend two short trident lines over 3 – 5 spans to the new 132/33kV substation to establish a looped connection to the substation off the FFW circuit. e. Modify the existing protection and telecommunication equipment at Fort Augustus 132kV substation to suit the new teed connection at Millennium South. | 30/09/2016
|  | SHETL-RI-002 & SPT-RI-001A | Millennium South 132/33kV Substation | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 30/09/2016
|  | SHETL-RI-044 | Millennium South 132/33kV Substation | Install a new 132kV OHL between Fort Augustus 132kV double busbar and SkyeTee. Connect the new 132kV OHL to a new 132kV circuit breakers at Fort Augustus. New 132kV Overhead line to be approximately 9km and to have a minimum rating equivalent to an ACSR lynx conductor at 50°C. Reinstate existing overhead line between Fort Augustus and Fort William. Modify any protection settings at Fort Augustus and Fort William for new arrangement. | 30/09/2016
Elgin Energy EsCo Limited | Milltown Airfield Solar Farm | SHETL-RI-099 | Elgin | Reconfigure the 132kV substation at Keith by installing a new 132kV busbar and connecting the Macduff circuits, the future Ault more circuit and relocating the existing Keith GT1 and GT3 to the new busbar. The new busbar at Keith will interface with the Keith - Macduff - Blackhillock project. | 31/10/2020
|  | SHETL-RI-073 | Elgin | Keith MacDuff Blackhillock 132kV Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kv transmission network by reconfiguring the transmission circuits away from Keith 132kV substation and increasing the supergrid capacity at Blackhillock substation. | 31/10/2020
|  | SHETL-RI-007c | Elgin | Blackhillock Substation Redevelopment — Redevelop Blackhillock Substation to enable the construction of new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by two 1200MVA 400/275kV SGTs and two 360MVA 275/132kV SGTs. Connect the existing three 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. | 31/10/2020
NuGeneration Ltd | Moorside | 32647LI | Moorside 400kV Substation | Reconductor Carr
|  | NGET-RI-30029S | Moorside 400kV Substation | Construct a new 15 bay Moorside 400kV GIS double substation to include 4 new feeder circuit bays, 4 busbar section bays, 2 busbar coupler bays, 3 skeletal GIS generator bays and 2 skeletal GIS SGT bays.
|  |  | Moorside 400kV Substation | Installation of Operational tripping scheme.
|  | NGET-RI-21637-1 | Moorside 400kV Substation | Construct new 400/132kV demand connection substation at Roosecote and Stainburn complete with new 400/132kV SGTs and also a 400kV GIS substation at Middleton, connected via a double turn-in of the Heysham - Quernmore Tee circuits with a series reactor on each of the new Heysham - Middleton circuits.
|  | NGET-RI-21637-2 | Moorside 400kV Substation | Construct a new 400kV double circuit overhead line Harker 400kV to Stainburn 400kV, Stainburn 400kV to Moorside 400kV, Moorside 400kV to Roosecote 400kV and the cable circuit in a new tunnel from Roosecote 400kV to Middleton 400kV.
|  | NGET-RI-15080 | Moorside 400kV Substation | Reconductoring of the Cellarhead - Macclesfield 400kV circuit with 2 x 620mm² GAP conductor.
|  | NGET-RI-21631-2 | Moorside 400kV Substation | Uprate the 275kV circuit from Penwortham to Kirkby via Washway Farm.
|  | NGET-RI-21631-1 | Moorside 400kV Substation | Install 2 x 400/132kV SGTs at Washway farm and 4 x 400/275kV interbus transformers at Kirkby.
|  | NGET-RI-21632-1 | Moorside 400kV Substation | Reconductor Penworth - Padiham 400kV circuit.
|  | NGET-RI-21644-1 | Moorside 400kV Substation | Increase the capacity of the existing Penwortham cables on the Heysham - Stanah - Penwortham circuits.
|  | 32643SI | Moorside 400kV Substation | uprate circuit breakers at Harker 275kv
|  | NGET-RI-32646LI | Moorside 400kV Substation | Reconductor Hambleton Tee - Penwortham 400kV circuits as well as Carrington - Penwortham 400kV circuit.
|  | NGET-RI-32640SI | Moorside 400kV Substation | Uprate circuit breakers at Penwortham 400kV substation, Daines 400kV substation, Harker 275kV substation, Kearsley 275kV substation, Fiddlers Ferry 275kV substation and Carrington 400kV substation.
|  | 32641SI | Moorside 400kV Substation | uprate circuit breakers at Carrington 400kv
|  | 32644SI | Moorside 400kV Substation | Uprate circuit breakers at Kearsley 275kv substation
|  | 32645SI | Moorside 400kV Substation | Uprate circuit breakers at Fiddlers Ferry 275kv
|  | 32642SI | Moorside 400kV Substation | uprate circuit breakers at Daines 400kv
Moray Offshore Renewables Ltd | Moray Firth Offshore Wind Farm | SHET-RI-105 | Moray Firth 220/33kV Platform 1 & 2 Offshore Substation | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 01/07/2019
|  | SHETL-RI-074 | Moray Firth 220/33kV Platform 1 & 2 Offshore Substation | Established a new 400kV double busbar arrangement close to New Deer in Aberdeenshire. The proposed New Deer substation is located west of Peterhead along the existing 275kV double circuit OHL between Peterhead and Blackhillock/Keith/Kintore (VH & VX1 circuits). Establish a new ten bay 400kV double busbar arrangement complete with one bus section, two bus couplers and busbar selections on all circuits. The 275kV OHL is proposed to be reinsulated to 400kV between Peterhead and Rothienorman. The project will be completed in two stages . The 400kV double busbar will be built with a 400/275kV transformer connected between each side of the double busbar. The bus couplers shall be run open and locked, resulting in one side of the double busbar operating at 400kV, with the other side operating at 275kV. The transformer will be re-utilised at Peterhead in the final 400kV configuration. | 01/07/2019
MORAY OFFSHORE WINDFARM (WEST) LIMITED | Moray Offshore West Windfarm | SHET-RI-105 | Moray Firth 220/33kV Platform 1 & 2 Offshore Substation | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | 31/03/2024
EDF Energy Renewables Limited | Muaitheabhal Wind Farm | Muaitheabhal Item 1 | Muaitheabhal 132/33kV Substation | The Relevant Transmission Licensee will install a 13km wood pole overhead line between Muaitheabhal Windfarm and the proposed 132kV switching station near Balallan (to be established under SHET-RI-043), with two 132kV circuit switchers at Muaitheabhal Windfarm and a 132kV circuit breaker at Balallan 132kV switching station.
|  | SHETL-RI-007B | Muaitheabhal 132/33kV Substation | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays.
|  | SHETL-RI-042 | Muaitheabhal 132/33kV Substation | Western Isles HVDC Link — Establish a 600MW HVDC link with associated equipment and converter stations between the Western Isles (Arnish on Lewis) and the 400kV double busbar at Beauly (SHETL-RI-007b). The HVDC cable to be routed approximately 79km subsea cable, and approximately 80km by land cable. The HVDC infrastructure interface with a new 132kV double busbar at Arnish (Lewis) and the 400kV double busbar at Beauly.
|  | SHET-RI-043 | Muaitheabhal 132/33kV Substation | Lewis Infrastructure - Build a new 132kV single circuit OHL between Arnish substation, and the Muaitheabhal Tee point. Dismantle the existing 132kV single circuit OHL between Stornoway Tee point, and the Muaitheabhal Tee point.
Green Cat Renewable Developments Ltd | Navidale Wind Farm | SHETL-RI-035 | Brora GSP | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs. | 31/10/2021
|  | SHETL-RI-109 | Brora GSP | Loch Buidhe — Spittal 132kv Reconductoring - Reconductor the existing 90km 132kV tower line between Loch Buidhe and Spittal substations. The 132kV overhead line is to be reconductored with a higher capacity conductor than the existing conductor, and should have a minimum summer pre4ault rating of 176MvA. | 31/10/2021
|  | SHETL-RI-007C | Brora GSP | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | 31/10/2021
|  | SHETL-RI-031 | Brora GSP | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). | 31/10/2021
Neart Na Gaoithe Offshore Wind Ltd | Neart Na Gaoithe Offshore Wind Farm |  |  | Completion of all associated protection and control works.
All associated miscellaneous and minor works, including provision of Category 2 intertripping scheme and Category 4 intertripping scheme, as defined in the Grid code.
Extension of the existing Crystal Rigs 400kV substation and the installation of 400kV plant and apparatus which will form the connections to the two Transmission Interface Points, including busbars, circuit breakers, disconnectors, earth switches, surge arresters, current and voltage transformers.
Modification of the existing bus coupler and associated plant and apparatus at Crystal Rig 400kV substation, including relocation of the existing 400kV circuit breaker X130.
Provide communications, alarms, indications and metering.
South Eastern Power Networks | Ninefield | NGET-RI-11642 |  | Hotwiring of the Lovedean - Ninfield - Bolney circuits to increase their thermal rating.
|  | NGET-RI-21588 |  | Re-conductor the Dungeness - Sellindge OHL circuits to increase capacity.
|  | NGET-RI-30967 & NGET-RI-30968 |  | Construction of a new Sellindge double busbar bypass 400kV Substation.
|  | NGET-RI-31338, NGET-RI-31339 & NGET-RI-21497-5 |  | Installation of Flexible AC Transmission Solutions (FACTS) at Bolney, Ninfield and Richborough and associated works.
NLEI Limited | North Lowther Energy Initiative | NLEI Item 1 |  | Installation of a 275kV and 132kV switchbay at Elvanfoot substation, connecting to a 240MVA 275/132kV transformer (SGT2D). | 31/10/2022
|  | NLEI Item 2 |  | Installation of approximately 14km overhead line between Elvanfoot 132kV substation and NLEI wind farm. | 31/10/2022
|  | NLEI Item 3 |  | Installation of two 132kV line isolators at NLEI Wind Farm. | 31/10/2022
NorthConnect KS | Norway Interconnector | NGET-2GW | Peterhead 400KV | Install a 2GW HVDC converter station with associated equipment. HVDC cables to be routed into the sea and north towards Scotland. | 31/12/2022
|  | NGET-RI-30204 & SHETL-RI-025B | Peterhead 400KV | Construct a 2GW East Coast HVDC Link between Aberdeenshire and North East England. | 31/12/2022
|  | NGET-RI-30669-1 & SHETL-RI-033 | Peterhead 400KV | Install a second 2GW HVDC converter station with associated equipment. HVDC cables to be routed between Aberdeenshire and North East England. | 31/12/2022
National Grid NS Link Ltd | NS Link | NGET-RI-31154L1 | Blyth | New Blyth 400kV substation OHL turn-in works. | 30/09/2020
|  | NGET-RI-31154L2 | Blyth | Hotwire 275kV circuits in the North East. | 30/09/2020
|  | NGET-RI-31154S1 | Blyth | Build a new 400kV substation at Blyth. | 30/09/2020
Scottish & Southern Electricity Power Distribution | Nursling | NGET-RI-30752 |  | Creation of a new South West Operational Tripping Scheme (OTS) at Taunton.
|  | NGET-RI-31671-1 |  | Re-conductor the Bramley - Fleet OHL circuits to increase capacity.
|  | NGET-RI-31671-2 |  | Re-conductor the Fleet - Lovedean OHL circuits to increase capacity.
Horizon Nuclear Power Oldbury Ltd | Oldbury C | 20900S | Oldbury-on-Severn 400kV Substation | Construction of a new 400kV substation at close proximity to the company's existing Sealing End Compound at Aust on the 4YX route (Clifynydd - Whitson Seabank and Clifynydd - Imperial Park - Melksham). | 01/06/2029
|  | 20902L1 | Oldbury-on-Severn 400kV Substation | Re-conductor 2VL Route. | 01/06/2029
|  | 21348L | Oldbury-on-Severn 400kV Substation | Create a new Seabank - Oldbury on Severn 400kV circuit and a new Oldbury on Severn - Melksham 400kV circuit. | 01/06/2029
|  | 21348S | Oldbury-on-Severn 400kV Substation | Oldbury on Severn substation works: two feeder bays, one bus coupler, two bus sections, one skeletal generator bay, one skeletal station transformer bay and system to generator intertrip scheme. | 01/06/2029
Paul's Hill II Limited | Paul's Hill II Wind Farm | SHETL-RI-073 | Glenfarclas 132/33kV Substation | Keith MacDuff Blackhillock 132kV Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kv transmission network by reconfiguring the transmission circuits away from Keith 132kV substation and increasing the supergrid capacity at Blackhillock substation. | 31/10/2021
|  | SHETL-RI-015a | Glenfarclas 132/33kV Substation | Knocknagael – Tomatin 275/132kV Reinforcement - Reinforce the existing 132kV transmission network between Beauly–Farr–Boat of Garten (Circuits BR1/RG1/BR2/RG2). Note that the existing 132kV OHL passes close to Knocknagael substation. Establish a new 275/132kV substation station including a 132kV double busbar arrangement near Tomatin and connected to a new 275kV double circuit OHL from the Knocknagael 275kV busbar via 275/132kV SGTs. | 31/10/2021
|  | SHETL-RI-015b | Glenfarclas 132/33kV Substation | Beauly-Farr-Boat of Garten 132kV OHL Reconfiguration - The existing section of 132kV OHL (BR1 & BR2) between Beauly and Farr will be terminated on the 132kV busbar at Knocknagael Substation. The OHL sections of the existing 132kV OHL will be dismantled between Knocknagael and Farr as part of the 132kV OHL reconfiguration. The existing section of double circuit 132kV OHL (RG1 & RG2) between Farr and Boat of Garten will be reconfigured as radial circuits between Tomatin and Boat of Garten. A normally open (N/O) point will be required at Keith on the circuit (FK) between Glenfarclas and Keith. This arrangement will leave Glenfarclas on a radial circuit fed from Boat of Garten under normal operating conditions. | 31/10/2021
|  | SHETL-RI-007C | Glenfarclas 132/33kV Substation | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | 31/10/2021
Pencloe Wind Energy Ltd | Pencloe Windfarm | SPT-RI-007 | Pencloe 132/33kV | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction.
|  | SPT-RI-115 | Pencloe 132/33kV | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill substation heading east to 132kV Black Hill Substation. Black Hill substation will include three new 132kV circuit breakers (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation.
|  | SPT-RI-116B | Pencloe 132/33kV | Construction of Black Hill 132/33kV Substation including two 132kV circuit breakers (double busbar), two 132/33kV 90MVA transformers and 33kV B switchboard (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation.
|  | SPT-RI-114 | Pencloe 132/33kV | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV Meikle Hill Collector Substation, heading east to 132kV Dun Hill Substation. These works will be required in response to new generation connections in the vicinity of Dun Hill substation.
|  | SPT-RI-142 | Pencloe 132/33kV | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor.
Pentland Road Windfarm Ltd | Pentland Road | SHETL-RI-007B | Stornoway | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays.
|  | SHETL-RI-042 | Stornoway | Western Isles HVDC Link — Establish a 600MW HVDC link with associated equipment and converter stations between the Western Isles (Arnish on Lewis) and the 400kV double busbar at Beauly (SHETL-RI-007b). The HVDC cable to be routed approximately 79km subsea cable, and approximately 80km by land cable. The HVDC infrastructure interface with a new 132kV double busbar at Arnish (Lewis) and the 400kV double busbar at Beauly.
|  | SHETL-RI-043 | Stornoway | Establish transmission infrastructure between a new 132kV double busbar a Gravir and a new 132kV double busbar arrangement at Stornoway GSP. The new 132kV infrastructure to be a mixture of cable and overhead lines routed approximately 22km by subsea and 6km by land. Interface the new 132kV infrastructure at Stornoway Grid with the 33kV network via 2 x 60MVA transformers and the existing 132kV overhead line from Harris.
|  | SHETL-RI-055 | Stornoway | A compound will be established on the route of the existing 132kV Stornoway/Harris wood pole line at a suitable location to accommodate a new 132kV wood pole line from the newly established 132kV double busbar at Gravir. The new 132kV overhead line will be around 10km and have a minimum continuous rating of 150MVA. Two 132kV circuit breakers will be accommodated in the compound around the selected Tee point. A fully equipped 132kV feeder bay will be required at Gravir substation.
Pogbie Wind Farm Limited | Pogbie Wind Farm | None identified at this time | Pogbie 33kV Substation
Progress Power Ltd | Progress Power Station | NGET-RI-32473LI & NGET-RI-32473CI | Yaxley 400kV Substation | Installation of new terminal towers on the Norwich - Bramford circuits and removal of the existing suspension towers. Installation of the cable circuit to duck tee connection underneath OHL. | 30/09/2019
|  | NGET-RI-32473SI | Yaxley 400kV Substation | Installation of a new double busbar 400kV substation with associated feeder bays, coupler bay and skeleton generator bay and provide double tee connection of the new substation to the Norwich - Bramford double OHL circuit. | 30/09/2019
DONG Energy RB (UK) Limited | Race Bank Wind Farm | NGET-RI-20059 | Race Bank 132/33kV Substation | To extend Walpole 400kV busbars for connection of two generator bays and to modify existing busbar protection to include the new generation.
|  | NGET-RI-11122 | Race Bank 132/33kV Substation | Asset replacement of Walpole 132kV substation with a new GIS substation removing fault level restrictions currently precluding further 400kV and 132kV fault infeed at or near Walpole.
Rothes III Limited | Rothes III Wind Farm | SHETL-RI-007C | Dallas 275/33kV Substation | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | 31/05/2021
WKN Sallachy Ltd | Sallachy Wind Farm | SHETL-RI-035 | Sallachy 132kV Substation | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs.
|  | SHETL-RI-052 | Sallachy 132kV Substation | Establish a new 132kV double busbar arrangement at Lairg and build approximately 20km of new double circuit 132kV overhead tower line between Lairg and Loch Buidhe. It is expected that the first 10.5km of the new double circuit 132kV between Lairg and Loch Buidhe will be along the route of the existing Lairg - Shin (CS) 132kV OHL. A new route will have to be established for the remaining 9.5km (approx.) double circuit 132kV OHL.
|  | SHETL-RI-032A | Sallachy 132kV Substation | A new 275kV overhead line and substation works between Dounreay, Thurso and Spittal Substations.
|  |  | Sallachy 132kV Substation | Erect a single 132kV wood pole line over a distance of approximately 6km between the 132/33kV substation facility at the Glenmorie windfarm development site and the new Relevant transmission licensee's 275/132kV substation at Fyrish. The 132kV line will be built using portal wood pole 'H' type construction, and stung with 150mm ACSR conductors to meet the Windfarms connection capacity. Some minor circuit under grounding maybe required along the final circuit route.
|  |  | Sallachy 132kV Substation | At Cassley 132/33kV substation install a 132kV feeder circuit breaker bay and connected off the incoming 132kV line which terminates with the substation compound. The bay will include a single 132kV circuit breaker unit, a single 132kV line disconnector and associated busbar extension, support structure, protection, control and metering equipment. The incoming 132kV line circuit from Sallachy will terminate on support structures adjacent to the 132kV circuit breaker.
|  |  | Sallachy 132kV Substation | Replace the Cassley 132kV transformer disconnector with a modern equivalent 132kV circuit switcher device.
|  |  | Sallachy 132kV Substation | At the new Sallachy 132/33kV substation install a 132kV transformer circuit switcher.
|  | SHETL-RI-007C | Sallachy 132kV Substation | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars.
|  | SHETL-RI-031 | Sallachy 132kV Substation | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster).
Sandy Knowe Wind Farm Ltd | Sandy Knowe Wind Farm |  | Glenglass 132/33kv | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | 30/10/2021
|  | SPT-RI-007 | Glenglass 132/33kv | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction. | 30/10/2021
|  | SPT-RI-158 | Glenglass 132/33kv | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 30/10/2021
|  | SPT-RI-115 | Glenglass 132/33kv | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill substation heading east to 132kV Black Hill Substation. Black Hill substation will include three new 132kV circuit breakers (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 30/10/2021
|  | SPT-RI-022 | Glenglass 132/33kv | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | 30/10/2021
|  | SPT-RI-186 | Glenglass 132/33kv | Installation of an overhead protection scheme at Kilmarnock South 400/275kV substation. | 30/10/2021
|  | Sandy Knowe Item 2 | Glenglass 132/33kv | Installation of 132kV overhead line (approximately 6.5km), and an optical fibre, between Glenglass 132/33kV substation and Sandy Knowe wind farm substation. | 30/10/2021
|  | Sandy Knowe Item 3 | Glenglass 132/33kv | From the Sandy Knowe wind farm 132kV circuit installation of one line isolator. | 30/10/2021
|  | SPT-RI-114 | Glenglass 132/33kv | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV Meikle Hill Collector Substation, heading east to 132kV Dun Hill Substation. These works will be required in response to new generation connections in the vicinity of Dun Hill substation. | 30/10/2021
|  | SPT-RI-173 | Glenglass 132/33kv | There is currently 246MW (259MVA, including 132kV and 33kV connections) contracted at the proposed Glenglass 132kV substation. In order to facilitate the currently contracted 132kV generation connections at Glenglass 132kV substation, it is proposed to install a new 132kV eight bays (for two new wind farm connections), GIS double busbar at Glenglass. The new eight bays double busbar substation will provide two 132/33kV transformers, two 132kV incomers, one bus coupler and two 132kV circuit breakers for the contracted wind farms. | 30/10/2021
|  |  | Glenglass 132/33kv | At Glenglass 132/33kV substation a new 132kV double switchbay (consisting of five line isolators and two circuit breakers owned by the relevant transmission licensee) and associated apparatus will be installed. | 30/10/2021
|  | SPT-RI-142 | Glenglass 132/33kv | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/10/2021
|  | SPT-RI-143 | Glenglass 132/33kv | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. | 30/10/2021
Sanquhar II Community Wind Company Limited | Sanquhar II Wind Farm |  | Sanquhar 132/33kV | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement.
|  | SPT-RI-007 | Sanquhar 132/33kV | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction.
|  | SPT-RI-158 | Sanquhar 132/33kV | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014.
|  | SPT-RI-115 | Sanquhar 132/33kV | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill substation heading east to 132kV Black Hill Substation. Black Hill substation will include three new 132kV circuit breakers (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation.
|  | SPT-RI-022 | Sanquhar 132/33kV | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section.
|  | SPT-RI-186 | Sanquhar 132/33kV | Installation of an overhead protection scheme at Kilmarnock South 400/275kV substation.
|  | SPT-RI-114 | Sanquhar 132/33kV | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV Meikle Hill Collector Substation, heading east to 132kV Dun Hill Substation. These works will be required in response to new generation connections in the vicinity of Dun Hill substation.
|  | SPT-RI-173 | Sanquhar 132/33kV | There is currently 246MW (259MVA, including 132kV and 33kV connections) contracted at the proposed Glenglass 132kV substation. In order to facilitate the currently contracted 132kV generation connections at Glenglass 132kV substation, it is proposed to install a new 132kV eight bays (for two new wind farm connections), GIS double busbar at Glenglass. The new eight bays double busbar substation will provide two 132/33kV transformers, two 132kV incomers, one bus coupler and two 132kV circuit breakers for the contracted wind farms.
|  |  | Sanquhar 132/33kV | At Glenglass 132/33kV substation a new 132kV double switchbay (consisting of five line isolators and two circuit breakers owned by the relevant transmission licensee) and associated apparatus will be installed.
|  | SPT-RI-142 | Sanquhar 132/33kV | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor.
|  | SPT-RI-143 | Sanquhar 132/33kV | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation.
Sanquhar II Community Wind Company Limited | Sanquhar IIa Community Wind Farm | SPT-RI-007 |  | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction. | 30/11/2023
|  | SPT-RI-158 |  | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | 30/11/2023
|  | SPT-RI-225 |  | It is proposed to connect Glenmuckloch pump storage 132kV collector substation to New Cumnock 132kV Board C substation via a 22km wood pole overhead line circuit. It is proposed to install a High Temperature Low Sag (HTLS) conductor on the circuit to provide sufficient capacity for the connection of two developments, namely Glenmuckloch pump storage (100MW) and Sanquhar IIA wind farm (99MW). The length of the circuit is approximately 22km and will require a 132kV bay at New Cumnock. The anticipated capability of the circuit will be as in the table below. | 30/11/2023
|  | Sanquhar IIa Item 1 |  | At Sanquhar II Wind Farm 132kV substation installation of one line isolator. | 30/11/2023
|  | SPT-RI-176 |  | 10. New Cumnock Overload Protection Scheme - To utilise the non-firm capacity at New Cumnock and the 132kV network in South West Scotland an overload protection scheme is required at New Cumnock substation to monitor the loading on the 275kV circuits from Coylton, supergrid transformers and 132kV circuits at New Cumnock to prevent any overloading on the transmission system. The scheme at New Cumnock will communicate with remote systems at Dunhill, Blackhill, Glenglass and Kendoon North substations to trigger tripping signals to generators connected at these substations. | 30/11/2023
|  | SPT-RI-186 |  | Installation of an overhead protection scheme at Kilmarnock South 400/275kV substation. | 30/11/2023
|  | Sanquhar IIa Item 3 |  | At Glenmuckloch pump storage 132kV substation, a new (Relevant Transmission Licensee owned) 132kV circuit breaker and 132kV isolators and associated apparatus, will be installed. | 30/11/2023
|  | Sanquhar IIa Item 4 |  | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | 30/11/2023
|  | Sanquhar IIa Item 2 |  | Installation of 132kV wood pole overhead line (approximately 8km), and an optical fibre, between Sanquhar II wind farm 132kV substation and Glenmuckloch pump storage 132kV substation. | 30/11/2023
|  | SPT-RI-142 |  | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/11/2023
|  | SPT-RI-143 |  | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. | 30/11/2023
Sanquhar Community Wind Company Limited | Sanquhar Wind Farm | SPT-RI-007 | Ulzieside 132/33kV | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction. | 02/10/2020
|  | SPT-RI-115 | Ulzieside 132/33kV | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill substation heading east to 132kV Black Hill Substation. Black Hill substation will include three new 132kV circuit breakers (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | 02/10/2020
|  | SPT-RI-022 | Ulzieside 132/33kV | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | 02/10/2020
|  | SPT-RI-114 | Ulzieside 132/33kV | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV Meikle Hill Collector Substation, heading east to 132kV Dun Hill Substation. These works will be required in response to new generation connections in the vicinity of Dun Hill substation. | 02/10/2020
|  | SPT-RI-142 | Ulzieside 132/33kV | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 02/10/2020
Community Wind Power Ltd | Scoop Hill Wind Farm | Scoop Hill Item 1 | Scoop Hill Wind Farm 132kV Substation | At Moffat 132kV substation install two 132kV feeder circuit breakers and associated switch bays. | 31/12/2023
|  | SPT-RI-229 | Scoop Hill Wind Farm 132kV Substation | A new 400/132kV 240MVA transformer, and associated 400kV and 132kV circuit breaker bays, shall be installed at Moffat 400/132kV substation to increase the available generation capacity at the 132kV substation. | 31/12/2023
|  | Scoop Hill Item 2 | Scoop Hill Wind Farm 132kV Substation | Establish 2x 132kV circuit, incorporating 10km of underground cable and associated auxiliary cable, between Moffat 132kV Substation and Scoop Hill Wind Farm Substation | 31/12/2023
|  | Scoop Hill Item 3 | Scoop Hill Wind Farm 132kV Substation | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of this Bilateral Connection Agreement. | 31/12/2023
Seabank Power Ltd | Seabank 3 | 20900S | Seabank 400kV Substation | Construction of a new 400kV substation at close proximity to the company's existing Sealing End Compound at Aust on the 4YX route (Clifynydd - Whitson Seabank and Clifynydd - Imperial Park - Melksham).
EDF Energy Nuclear Generation Ltd | Sizewell C | 20834-2 | Sizewell North 400kV Substation | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design. | 31/10/2019
|  | 20315S | Sizewell North 400kV Substation | Construct an initial 9 bay 400kV GIS substation at Bramford as a 2 section substation with one bus coupler and two bus sections to be subsequently extended by a further section turning in existing Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits. | 31/10/2019
|  | NGET-RI-20834-1 | Sizewell North 400kV Substation | Installation of two 400kV 3000MVA reactors in the existing Sizewell 400kV GIS substation site by utilizing and populating the four spare bays on the existing GIS originally identified for future nuclear generator station and unit transformer connections. | 31/10/2019
Sneddon Law Community Wind Company Limited | Sneddon Law Wind | Sneddon Law Item 1 | Kilmarnock Town 275/33kV | Installation and commissioning of a protection scheme to interface with the relevant transmission licensee's protection scheme(s) identified in one off works and relay a signal to the user's wind farm substation in order to disconnect the user's wind farm. These works will need to be completed by the host distribution network operator. | 31/10/2018
|  | SPT-RI-143 | Kilmarnock Town 275/33kV | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. | 31/10/2018
RES UK & Ireland Limited | Solwaybank | None identified at this time | Chapelcross 132/33Kv Substation
Islay Tidal Power Limited | Sound of Islay Tidal | None identified at this time | Port Ann GSP |  | 30/11/2017
Vattenfall Wind Power Ltd | South Kyle | SPT-RI-007 | New Cummock 132/33kV | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction. | 01/06/2019
|  | SPT-RI-142 | New Cummock 132/33kV | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 01/06/2019
Spalding Energy Expansion Limited | Spalding Energy Expansion | NGET-RI-21339S | Spalding | • To provide one generator bay. • To modify existing busbar protection to include the new generation connection. • To install ancillary services monitoring equipment.
|  | NGET-RI-21765-1 | Spalding | Extend and convert the existing Bicker Fen 400kV substation to a double busbar AIS substation with 4 feeder bays, 2 transformer bays, 1 bus coupler bays and 2 skeleton bus section bays to accommodating the existing 4 circuits and 2 transformers. Build 4 feeder bays, 2 transformer bays and one bus coupler and fully equip these bays. Modify the existing protection scheme to include 4 feeders, 2 transformers and one bus coupler.
Speyside Renewable Energy Partnership Ltd | Speyside CHP | Speyside CHP item 1 | Keith 132/33kV | Install a fourth 90MVA 132/33kV Grid Transformer, 1 x 132kV circuit breaker bay and 1 x 33kV transformer incomer circuit breaker at the Keith Grid Supply Point Substation.
|  | SHETL-RI-047 | Keith 132/33kV | Bulk purchase of the series reactor at Killingholme 400kV Substation.
|  | SHETL-RI-004 | Keith 132/33kV | Reconductor the Beauly - Foyers - Blackhillock 275kV double circuit line with larger capacity conductor between Beauly - Knocknagael and between Knocknagael - Blackhillock and Blackhillock - Kintore (XH1/XH2). The substation at Knocknagael is adjacent to the existing Foyers line tee point.
Elgin Energy EsCo Limited | Speyslaw Solar | SHETL-RI-099 | Elgin | Reconfigure the 132kV substation at Keith by installing a new 132kV busbar and connecting the Macduff circuits, the future Ault more circuit and relocating the existing Keith GT1 and GT3 to the new busbar. The new busbar at Keith will interface with the Keith - Macduff - Blackhillock project. | 31/10/2020
|  | SHETL-RI-073 | Elgin | Keith MacDuff Blackhillock 132kV Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kv transmission network by reconfiguring the transmission circuits away from Keith 132kV substation and increasing the supergrid capacity at Blackhillock substation. | 31/10/2020
|  | SHETL-RI-007c | Elgin | Blackhillock Substation Redevelopment — Redevelop Blackhillock Substation to enable the construction of new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by two 1200MVA 400/275kV SGTs and two 360MVA 275/132kV SGTs. Connect the existing three 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. | 31/10/2020
Lewis Wind Power Ltd | Stornoway Wind Farm | SHETL-RI-007B | Stornoway 132/33kV Substation | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays.
|  | SHETL-RI-042 | Stornoway 132/33kV Substation | Western Isles HVDC Link — Establish a 600MW HVDC link with associated equipment and converter stations between the Western Isles (Arnish on Lewis) and the 400kV double busbar at Beauly (SHETL-RI-007b). The HVDC cable to be routed approximately 79km subsea cable, and approximately 80km by land cable. The HVDC infrastructure interface with a new 132kV double busbar at Arnish (Lewis) and the 400kV double busbar at Beauly.
|  | Stornoway Item 1 | Stornoway 132/33kV Substation | The Relevant Transmission Licensee will construct a 5km single circuit 132kV wood pole overhead line from a fully equipped 132kV feeder bay at Arnish 132kV substation to the windfarm site. The new 132kV line will terminate on the Relevant Transmission’s 132kV line isolator at the User’s 132/33kV windfarm substation.
EDF Energy Renewables Limited | Stranoch Wind Farm | SPT-RI-205 | Stranoch Wind 132/33KV | Installation of approximately 1km of 132kV overhead line between Chirmorie Wind Farm substation and the tee point on the Mark Hill to Stranoch wind farm overhead line, a 132kV isolator at Chirmorie wind farm substation and 132kV substation at Mark Hill and a 132kV switch bay will be installed. From this a 132kV circuit consisting 0.5km of underground cable and 13.5 of 132kV overhead line 300mm UPAS conductor) will be installed to the overhead line tee point connecting the circuits to Chirmorie and Stranoch wind farms. | 31/10/2017
|  | SPT-RI-206 | Stranoch Wind 132/33KV | At Mark Hill substation a 275kV switchbay will be installed to control a 275/132kV 240MVA transformer (SGT3). This will connect to a 132kV busbar (B Board) provided for the connection of renewable generation. | 31/10/2017
|  | SPT-RI-186 | Stranoch Wind 132/33KV | Installation of an overhead protection scheme at Kilmarnock South 400/275kV substation. | 31/10/2017
|  | Stranoch Part 1 | Stranoch Wind 132/33KV | 1. Installation of approximately 7.5km of 132kV overhead line from the Stranoch Wind Farm site to the Chirmorie Wind Farm tee point. 2. Installation of a 132kV line isolator at Stranoch Wind Farm substation. | 31/10/2017
|  | SPT-RI-142 | Stranoch Wind 132/33KV | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 31/10/2017
|  | SPT-RI-143 | Stranoch Wind 132/33KV | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. | 31/10/2017
ILI (Strathaven South) Ltd | Strathaven South Dedicated Line | SPT-RI-155 | Linnmill Substation | Replace the 3.2km 132kV undergroud cable section on the Coalburn to Linmill No.1 132kV circuit.
SSE Generation Ltd | Strathy North and South Wind | SHETL-RI-035 | Strathy North and Strathy South 132/33kV Substation | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs. | 12/06/2015
|  | SHETL-RI-036 | Strathy North and Strathy South 132/33kV Substation | Reconductor part of the first 275kV circuits (BT1 - Beauly - Kilbraur - Gordonbush - Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substation (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay. | 12/06/2015
|  | SHETL-RI-058 | Strathy North and Strathy South 132/33kV Substation | Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe (Cambusmore) 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include two new Super Grid Transformers to connect Shin 132kV substation, new double circuit steel lattice tower L3/1 construction approximately 40km and works Beauly and Loch Buidhe 275kV substations. | 12/06/2015
|  | SHETL-RI-060 | Strathy North and Strathy South 132/33kV Substation | Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay (LT1/TD1/DU1) making it the same specification as the east side (LY2/YU2). | 12/06/2015
|  | SHETL-RI-032A | Strathy North and Strathy South 132/33kV Substation | A new 275kV overhead line and substation works between Dounreay, Thurso and Spittal Substations. | 12/06/2015
|  | SHETL-RI-007C | Strathy North and Strathy South 132/33kV Substation | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | 12/06/2015
|  | SHETL-RI-031 | Strathy North and Strathy South 132/33kV Substation | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). | 12/06/2015
E.ON Climate & Renewables UK Developments Limited | Strathy Wood | SHETL-RI-035 | Strathy Wood | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs. | 31/10/2021
|  | SHETL-RI-036 | Strathy Wood | Reconductor part of the first 275kV circuits (BT1 - Beauly - Kilbraur - Gordonbush - Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substation (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay. | 31/10/2021
|  | SHETL-RI-058 | Strathy Wood | Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe (Cambusmore) 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include two new Super Grid Transformers to connect Shin 132kV substation, new double circuit steel lattice tower L3/1 construction approximately 40km and works Beauly and Loch Buidhe 275kV substations. | 31/10/2021
|  | SHETL-RI-060 | Strathy Wood | Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay (LT1/TD1/DU1) making it the same specification as the east side (LY2/YU2). | 31/10/2021
|  | SHETL-RI-106 | Strathy Wood | Connagil 2nd SGT - At Connagill substation, install a 2nd 275/132kV 360MVA supergrid transformer, to enable the connection of wind generation in the local area to the Dounreay – Loch Buidhe 275kV circuit.. | 31/10/2021
|  | SHETL-RI-032A | Strathy Wood | A new 275kV overhead line and substation works between Dounreay, Thurso and Spittal Substations. | 31/10/2021
|  | Strathy Wood Part 1 | Strathy Wood | 1. Construct a 132kV wood pole trident line over a distance of 5km between Strathy North 132/33kV substation and the new 132/33kV substation at Strathy Wood. The wood pole line will be coupled off one of the incoming 132kV line circuits at Strathy North 132kV substation, and terminated on a new 132kV transformer disconnector switch at Strathy Wood 132/33kV substation. 2. Provision and installation of a 132kV transformer circuit switcher (115) at Strathy Wood 132/33kV substation, installed on the 132kV side of the 132/33kV transformer unit. | 31/10/2021
|  | SHETL-RI-007c | Strathy Wood | Blackhillock Substation Redevelopment — Redevelop Blackhillock Substation to enable the construction of new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by two 1200MVA 400/275kV SGTs and two 360MVA 275/132kV SGTs. Connect the existing three 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. | 31/10/2021
|  | SHETL-RI-031 | Strathy Wood | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). | 31/10/2021
SSE Generation Ltd | Stronelairg | SHETL-RI-085 | Stronelairg 132/33kV Substation | Establish a new 400/132kV Substation at Melgarve to allow the connection of wind generation in the area. | 31/03/2017
|  | SHETL-RI-092 | Stronelairg 132/33kV Substation | Establish a new 132kV cable circuit between Melgarve substation and a new 132kV busbar at Stronelairg. | 31/03/2017
|  | SHETL-RI-069 | Stronelairg 132/33kV Substation | A Static VAR Compensators (SVC) is required at Tummel Bridge for voltage support on the 275kV Beauly-Denny overhead line. The SVC will have a capability of +225MVAr and -75MVAr. Extend the 275kV busbar at Tummel bridge to accommodate the SVC. | 31/03/2017
|  | SHETL-RI-002 & SPT-RI-001A | Stronelairg 132/33kV Substation | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 31/03/2017
SSE Renewables Developments (UK) Ltd | Tangy III Wind Farm |  | Carradale | At Carradale 132/33kV substation, the relevant transmission licensee shall replace the existing 2 x 60MVA 132/33kV transformers with higher rated 2 x 120MVA 132/33kV transformers within the same substation accommodation. The works include all associated plinth foundations, transformer protection equipment and cabling work associated with the installation of the replacement 120MVA 132/33kV transformers. The existing 132kV circuit switchers and associated 132kV cabling are adequately rated to meet the capacity of the new 120MVA 132/33kV transformers. However the existing 33kV transformer circuit breakers and associated 33kV cabling is not and will need to be replaced in order to meet the capacity of the new transformers. Minor modifications will require to be made to existing equipment to accommodate the larger transformer size, including earthing, fencing and substation equipment works. | 01/04/2022
|  | SPT-RI-028 | Carradale | Reconfigure and extend Dalmally 275kV substation to a double busbar arrangement. Associated civil works and other miscellaneous works, including installation/modification of associated protection, control, telecommunications and metering equipment and modification of the Operation Tripping Scheme associated with the connection of Inveraray 275kV Substation. | 01/04/2022
|  | SHETL-RI-013 | Carradale | Establish a new 275/132kV Substation (Ardbrecknich) near the existing Inveraray/Taynuilt 132kV line route with two 360 MVA 275/132kV transformers. Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275kV double circuit OHL between Ardbrecknish and Dalmally Substations. | 01/04/2022
|  | SHETL-RI-050 | Carradale | Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 84km of 132kV double circuit OHL steel lattice construction between Inveraray, Port An and Crossaig. | 01/04/2022
Thorpe Marsh Power Ltd | Thorpe Marsh | 21771 | Thorpe Marsh | Extend the 400kV AIS double busbar substation at Thorpe Marsh and all associated works. | 30/09/2020
|  | NGET-RI-20488S | Thorpe Marsh | Construct a new 400kV AIS double busbar substation at Thrope Marsh of 2 feeder bays, 1 generator bay and 1 bus coupler bay, on the site of the decommissioned part of the 275kV substation, extended to the North and West onto land currently owned by RWE Generation UK plc. | 30/09/2020
Nanclach Limited | Tom Nan Clach | SHETL-RI-015a | Boat of Garton | Knocknagael – Tomatin 275/132kV Reinforcement - Reinforce the existing 132kV transmission network between Beauly–Farr–Boat of Garten (Circuits BR1/RG1/BR2/RG2). Note that the existing 132kV OHL passes close to Knocknagael substation. Establish a new 275/132kV substation station including a 132kV double busbar arrangement near Tomatin and connected to a new 275kV double circuit OHL from the Knocknagael 275kV busbar via 275/132kV SGTs. | 31/03/2019
|  | SHETL-RI-015b | Boat of Garton | Beauly-Farr-Boat of Garten 132kV OHL Reconfiguration - The existing section of 132kV OHL (BR1 & BR2) between Beauly and Farr will be terminated on the 132kV busbar at Knocknagael Substation. The OHL sections of the existing 132kV OHL will be dismantled between Knocknagael and Farr as part of the 132kV OHL reconfiguration. The existing section of double circuit 132kV OHL (RG1 & RG2) between Farr and Boat of Garten will be reconfigured as radial circuits between Tomatin and Boat of Garten. A normally open (N/O) point will be required at Keith on the circuit (FK) between Glenfarclas and Keith. This arrangement will leave Glenfarclas on a radial circuit fed from Boat of Garten under normal operating conditions. | 31/03/2019
|  | SHETL-RI-007C | Boat of Garton | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | 31/03/2019
Wainstones Energy Ltd | Trafford Power | 33285 | Carrington 400kV | Re-conductor the Carrington to Daines 4 circuit (~2km) with 2 x 620mm² GZTACSR gap-type conductor at 170°C. | 30/09/2018
|  | 21619 - 11 | Carrington 400kV | Associated substation works for the turn-in including the Penwortham and Daines feeder bays and GIB runs to connect the Penwortham - Daines circuit (ZQ route) to the new 400kV substation. | 30/09/2018
|  | 21619 - 2 | Carrington 400kV | OHL turn in the Penwortham - Daines circuit into existing Carrington substation. | 30/09/2018
|  | 33285L | Carrington 400kV | Rephasing of the Carrington - Penwortham circuit. | 30/09/2018
|  | 21619-1 | Carrington 400kV | Extend the 400kV GIS double busbar substation at Carrington. | 30/09/2018
|  | 21619-1S | Carrington 400kV | Advance civil works at Carrington substation for Wainstones. | 30/09/2018
|  | 33285O | Carrington 400kV | Build one skeletal GIS bays for connection of the generation. | 30/09/2018
|  | 33285S | Carrington 400kV | Scheme Description Build and install a Category 1 intertrip to trip the generation for faults which overload the NETS and also two skeletal GIS bays for connection of the generation. Build and install a Category 1 intertrip to trip the generation for faults which overload the NETS and also two skeletal GIS bays for connection of the generation. | 30/09/2018
PNE Wind UK Ltd | Tralorg Wind Farm | SPT-RI-147 | Tralorg 33KV | A new 275kV double circuit overhead line will be constructed between Kilmarnock South and Coylton 275kV substation having a minimum summer pre-fault rating 1500MVA per circuit. In addition, the existing 132V circuit between Kilmarnock South and the Coylton T will be removed to facilitate a line routing for the third Kilmarnock South to Coylton 275kV circuit. Moreover, the Coylton 275/132kV SGT1 and SGT2 120MVA transformers will be replaced with 240MVA units to provide sufficient export capacity for the contracted generation in the area.
|  | SPT-RI-136 | Tralorg 33KV | Reconductor the 275kV single circuit overhead line (YY route) between Coylton 275kV substation and Mark Hill 275kV substation.
|  | SPT-RI-142 | Tralorg 33KV | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor.
|  | SPT-RI-143 | Tralorg 33KV | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation.
Triton Knoll Offshore Wind Farm Ltd | Triton Knoll Offshore Wind Farm | NGET-RI-21765S | Triton Knoll Offshore Substation | Extend Bicker Fen 400kV AIS double busbar substation with two additional skeleton generator bays. | 13/08/2019
|  | NGET-RI-21765-1 | Triton Knoll Offshore Substation | Extend and convert the existing Bicker Fen 400kV substation to a double busbar AIS substation with 4 feeder bays, 2 transformer bays, 1 bus coupler bays and 2 skeleton bus section bays to accommodating the existing 4 circuits and 2 transformers. Build 4 feeder bays, 2 transformer bays and one bus coupler and fully equip these bays. Modify the existing protection scheme to include 4 feeders, 2 transformers and one bus coupler. | 13/08/2019
Tullymurdoch Limited | Tullymurdoch Wind Farm |  | Coupar Angus | At Coupar Angus Grid Supply Point substation replace the two 132/33kV 45MVA grid transformers with two higher rated 132/33kV 120MVA transformer units. Undertake upgrades to the existing transformer plinths and foundations to accommodate the larger transformers. Replace the two existing 33kV 1250 amp outdoor transformer circuit breakers with two higher rated 33kV 2500 amp transformer incomer breakers. | 30/11/2016
|  | SHETL-RI-002 & SPT-RI-001A | Coupar Angus | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 30/11/2016
SCT Renewables Limited | Viking Wind Farm | SHETL-RI-053 | Kergord | It is required to construct a 600MW HVDC link from Shetland to the Scottish mainland at an HVDC switching station in the vicinity of Sinclair's Bay in Caithness. The HVDC switching station works will integrate with the Caithness-Moray Transmission Reinforcement. The HVDC link includes a 600MW HVDC converter station and 132kV substation at Kergord in Shetland. The new 132kV substation at Kergord will be the collection point for the large volume of wind generation in Shetland. The 600MW HVDC link will have approximately 13km of land cable and 284km of Subsea cable between Shetland and the HVDC switching station in Caithness.
|  | SHETL-RI-062 | Kergord | An HVDC switching station is required to integrate the Caithness - Moray transmission reinforcement and the Shetland connection. The HVDC switching station is proposed to be in the vicinity of Sinclair's Bay in Caithness. The HVDC switching station works will integrate with the Caithness - Moray transmission reinforcement and the Shetland HVDC link.
|  | SHETL-RI-007C | Kergord | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars.
|  | SHETL-RI-031 | Kergord | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster).
Wathegar 2 Limited | Wathegar 2 Windfarm | SHETL-RI-032B | Mybster 1 | Reinforce the existing 132kV double circuit overhead line between Dounreay, Thurso and Mybster substation (UTN/UTS and part of TME/TMW) Via a new 275/132kV substation at Spittal. | 31/12/2018
|  | SHETL-RI-035 | Mybster 1 | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs. | 31/12/2018
|  | SHETL-RI-036 | Mybster 1 | Reconductor part of the first 275kV circuits (BT1 - Beauly - Kilbraur - Gordonbush - Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substation (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay. | 31/12/2018
|  | SHETL-RI-037 | Mybster 1 | Establish a new 275/132kV Fyrish substation close to the existing Alness 132kV OHL Tee location. The substation shall interface with the 275kV double-circuit between Beauly and Loch Buidhe. An optimal 132kV route will be designed and engineered to link the new 275/132kV Fyrish substation with the existing Alness GSP. | 31/12/2018
|  | Wathegar 2 Item 3 | Mybster 1 | Install 2 x 132kV transformer circuit breaker bays connected off the Mybster 132kV busbar extension, complete with protection and associated auxiliary equipment. (The incumbent 33kV switchboard and 132kV transformer circuit switchers are adequately rated to meet the 120MVA transformer capacity; hence no further works are required). | 31/12/2018
|  | Wathegar 2 Item 1 | Mybster 1 | At the Mybster 132kV extension substation, install 2 x 132kV busbar disconnectors, associated busbar extensions, support structures, protection, control and metering equipment. | 31/12/2018
|  | SHETL-RI-002 & SPT-RI-001A | Mybster 1 | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | 31/12/2018
|  | Wathegar 2 Item 2 | Mybster 1 | At Mybster 132/33kV substation, the Relevant Transmission Licensee shall replace the existing 2 x 30 MVA and 1 x 60 MVA 132/33kV transformers with higher rated twin 120MVA 132/33kV transformers within the same substation accommodation. The works will include all associated plinth foundations, transformer protection equipment, and 33kV cabling work associated with the two replacement 120MVA transformers. | 31/12/2018
|  | SHETL-RI-032A | Mybster 1 | A new 275kV overhead line and substation works between Dounreay, Thurso and Spittal Substations. | 31/12/2018
|  | SHETL-RI-007C | Mybster 1 | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | 31/12/2018
|  | SHETL-RI-031 | Mybster 1 | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). | 31/12/2018
DP Marine Energy Limited | West Islay Tidal | SHETL-RI-011 | Carradale 132/33kV | Establish a new 132kV switching station at Crossaig in Kintyre, complete with busbar connected reactive compensation (SVC). Connect in the existing 132kV double circuit line to Port Ann. Rebuild and connect in the existing 132kV double circuit line to Carradale. Establish two 132kV AC subsea cable circuits between the new switching station at Crossaig and the existing 132kV busbar at Hunterston. Establish a second 132/33kV transformer substation at Carradale. Establish a third 400/132kV 360MVA inter-bus transformer at Hunterston. | 30/04/2019
Westray South Tidal Development Limited | Westray South | SHETL-RI-075A | Crook 132/33kV Substation | Establishment of the first 132kV transmission corridor on Orkney between Bay of Skaill and the new Finstown 132kV Busbar.
|  | SHETL-RI-075B | Crook 132/33kV Substation | Establishment of a 132kV Busbar at Crook and connection to Finstown substation via a 132kV Trident OHL.
|  | SHETL-RI-075C | Crook 132/33kV Substation | The establishment of a second 132kV OHL trident line between Bay of Skaill substation and Finstown substation.
|  | SHETL-RI-075D | Crook 132/33kV Substation | The establishment of a 132 kV trident OHL between Bay of Skaill (SHETL-RI-19) and the Crook 132 kV Busbar. Works will also include conversion of Crook 132 kV busbar to double busbar arrangement, and the installation of a 200 MVA quad booster with a bypass on the Finstown-Crook 132 kV circuit at Crook.
|  | SHETL-RI-025C | Crook 132/33kV Substation | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV.
|  | SHETL-RI-019 | Crook 132/33kV Substation | Establishment of a single 132kV AC circuit over a distance of approximately 70km between the proposed new 275kV GIS substation at Dounreay on the mainland and the new 132kV substation at the Bay of Skaill on Orkney. The 132kV circuit will comprise 9km of land cable and 91km of subsea cable element. Reactive compensation devices will be installed at both cable ends within the substation compounds at Dounreay and the Bay of Skaill. Two 33kV busbars complete with reactors will be installed and each connected to the 132kV busbars via two 120MVA 132/33kV GT's (four in total).
|  | SHETL-RI-020 | Crook 132/33kV Substation | Establish an HVDC link from Orkney to Peterhead in a phased manner to allow connection of marine and other renewable generation on and around the coast of Orkney. The works included in comprise an extension to the 132kV double busbar substation and a 600MW HVDC link from the northwest coast of Orkney to a HVDC switching station located inland in the vicinity of Sinclair’s Bay in Caithness. The HVDC link between Northwest Orkney and Sinclair’s Bay will have both land and subsea cable sections.
|  | SHETL-RI-021 | Crook 132/33kV Substation | Establish an HVDC link from Orkney to Peterhead in a phased manner to allow connection of marine and other renewable generation on and around the coast of Orkney. The works included in includes the 1200MW HVDC link to Peterhead and the HVDC switching station. The HVDC link between Northwest Orkney and Sinclair’s Bay will have both land and subsea cable sections.
|  | SHETL-RI-007C | Crook 132/33kV Substation | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars.
|  | SHETL-RI-031 | Crook 132/33kV Substation | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster).
Whitelaw Brae Windfarm Limited | Whitelaw Brae Windfarm | None identified at this time | Whitelaw Brae 'A' and 'B' 33kV Substations |  | 31/10/2019
Whiteside Hill Windfarm (Scotland) Limited | Whiteside Hill Wind Farm | SPT-RI-007 | Coylton | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction.
|  | SPT-RI-115 | Coylton | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill substation heading east to 132kV Black Hill Substation. Black Hill substation will include three new 132kV circuit breakers (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation.
|  | SPT-RI-022 | Coylton | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section.
|  | SPT-RI-101 | Coylton | Construct double circuit 132kV overhead line from New Cumnock 132kV substation to the new Windy Standard Collector Substation and at New Cumnock establish two new 132kV circuit breaker bays to facilitate the connection of the new circuits.
|  |  | Coylton | Construction of a 132kV double tee at Whiteside Hill 'T' point at the Whiteside Hill 132/33kV substation.
|  |  | Coylton | Establish a 132kV substation compound at the Whiteside Hill 132/33kV substation site along with 2 x 30MVA 132/33kV transformers with associated switchgear.
|  |  | Coylton | Establish a control/switchroom containing a 33kV double busbar switchboard and all protection/telecommunications apparatus required at the Whiteside Hill Substation site.
|  | SPT-RI-114 | Coylton | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV Meikle Hill Collector Substation, heading east to 132kV Dun Hill Substation. These works will be required in response to new generation connections in the vicinity of Dun Hill substation.
Scottish & Southern Electricity Power Distribution | Willesden |  |  | Provide two new tee circuits by banking them with outgoing feeders from 2 existing kV circuit breakers (Acton Lane GT1 & GT2 circuits) including GIS disconnector on each circuit.
Replace a short section of cable circuit of each of GT1 and GT2.
Good Energy Development (No.7) Limited | Willow Wind Farm | SHETL-RI-077 & SPT-RI-150 | Willow Wind 132/33kV | Establish a third 240MVA 220kV subsea cable circuit between Crossaig 132kV Substation and Hunterston 400kV Substation. | 01/04/2023
|  | SHETL-RI-011 | Willow Wind 132/33kV | Establish a new 132kV switching station at Crossaig in Kintyre, complete with busbar connected reactive compensation (SVC). Connect in the existing 132kV double circuit line to Port Ann. Rebuild and connect in the existing 132kV double circuit line to Carradale. Establish two 132kV AC subsea cable circuits between the new switching station at Crossaig and the existing 132kV busbar at Hunterston. Establish a second 132/33kV transformer substation at Carradale. Establish a third 400/132kV 360MVA inter-bus transformer at Hunterston. | 01/04/2023
Brockloch Rig Windfarm Ltd | Windy Standard II (Brockloch Rig 1) Wind Farm | SPT-RI-007 | Dun Hill 132/33kV Substation | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction. | 30/04/2017
|  | SPT-RI-145 | Dun Hill 132/33kV Substation | Construction of Dun Hill 132/33kV Substation including three 33kV circuit breakers, two 132/33kV 90MVA transformers and 33kV switchboard (double busbar). These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 30/04/2017
|  | SPT-RI-114 | Dun Hill 132/33kV Substation | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV Meikle Hill Collector Substation, heading east to 132kV Dun Hill Substation. These works will be required in response to new generation connections in the vicinity of Dun Hill substation. | 30/04/2017
Brockloch Rig III Limited | Windy Standard III Wind Farm | SPT-RI-007 | Dun Hill | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction. | 30/11/2019
|  | SPT-RI-145 | Dun Hill | Construction of Dun Hill 132/33kV Substation including three 33kV circuit breakers, two 132/33kV 90MVA transformers and 33kV switchboard (double busbar). These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | 30/11/2019
|  | SPT-RI-114 | Dun Hill | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV Meikle Hill Collector Substation, heading east to 132kV Dun Hill Substation. These works will be required in response to new generation connections in the vicinity of Dun Hill substation. | 30/11/2019
|  | SPT-RI-142 | Dun Hill | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | 30/11/2019
|  | SPT-RI-143 | Dun Hill | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. | 30/11/2019
Horizon Nuclear Power Wylfa Limited | Wylfa Newydd | NGET-RI-30106 | Wylfa 400kV Substation | Reconductor the Trawsfynydd legs of the Deeside - Trawsfynydd - Legacy circuits with GAP conductor.
|  | NGET-RI-30308 | Wylfa 400kV Substation | Install series compensation at Trawsfynydd 400kV Substation
|  | NGET-RI-30309 | Wylfa 400kV Substation | Installation of series compensation in the Pentir - Trawsfynydd 1 and Pentir - Trawsfynydd 2 circuits.
|  | NGET-RI-30311 | Wylfa 400kV Substation | Stage 1 - Establish a second 400kV circuit between Pentir and Trawsfyndd comprising following elements a) Establishing a new 400kV 3 bay single switch mesh AIS substation at Penisarwaun. This substation will connect the Pentir – Dinorwig 2 - Trawsfynydd 400kV circuits; b) Installation of approximately 6 km of 2 cores per phase XLPE cable to cross the Glaslyn Estuary. c) Reconductor the existing sections of OHL between Penisarwaun and Trawsfynydd with 2 x 700mm2. d) Connect the circuit into the existing disconnector bay on Mesh Corner 3 at Trawsfynydd 400kV substation. e) Installation of a F3 ferroresonance quenching scheme on the SGT 3 Disconnector. Stage 2 - Increase the thermal capability of the existing Pentir - Trawsfynydd 400kV circuit.
|  | NGET-RI-30310 | Wylfa 400kV Substation | Establish a new 400kV double circuit OHL route between the existing Wylfa substation and Pentir substation to create the Wylfa - Pentir 3 and Wylfa - Pentir 4 circuits.
|  | NGET-RI-30311-1L | Wylfa 400kV Substation | Increase the thermal capability of the existing Pentir - Trawsfynydd 400kV circuit.
|  | NGET-RI-30311-1S | Wylfa 400kV Substation | Increase the thermal capability of the existing Pentir - Trawsfynydd 400kV circuit.
|  | NGET-RI-30311-3C | Wylfa 400kV Substation | Increase the thermal capability of the existing Pentir - Trawsfynydd 400kV circuit.
|  | NGET-RI-30345 | Wylfa 400kV Substation | Reconfigure Wylfa 400kV substation by removing two SGTs and re-using the space to connect the new Wylfa-Pentir double circuit.
|  | NGET-RI-30346S | Wylfa 400kV Substation | Installation of a 2750MVA 2% impendence series reactor at Pentir 400kV substation
|  | NGET-RI-32589 | Wylfa 400kV Substation | Minor substation amendments at Wylfa 400kV.
|  | NGET-RI-32655 | Wylfa 400kV Substation | Installation of Operational tripping scheme.

## Scheme
Scheme Number | Scheme Description | Company Name | Connection Site | Generator Name | Connection Date
11630I | Reconductor the re-configured Norwich - Bramford (4YM route) with 3 x 700mm² AAAC conductor operating at 75°C. | East Anglia FOUR Limited | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | East Anglia 4 | 01/04/2027
|  | SMart Wind SPC5 Limited | Hornsea Platform 3A Offshore Substation | Hornsea Power Station 3A | 01/04/2023
|  | SMart Wind SPC6 Limited | Hornsea Platform 3B Offshore Substation | Hornsea Power Station 3B | 01/10/2023
|  | SMart Wind SPC7 Limited | Hornsea Platform 3C Offshore Substation | Hornsea Power Station 3C (Formally 4A) | 01/04/2024
|  | SMart Wind SPC8 Limited | Hornsea Platform 3D Offshore Substation | Hornsea Power Station 3D (formally 4B) | 01/10/2024
20315L | At Bramford 400kV substation carry out OHL and cable works to enable the turn in of the Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits. | East Anglia FOUR Limited | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | East Anglia 4 | 01/04/2027
|  | East Anglia THREE Limited | Platform EA3A and Platform EA3B 220/33kV Substations | East Anglia 3
20315S | Construct an initial 9 bay 400kV GIS substation at Bramford as a 2 section substation with one bus coupler and two bus sections to be subsequently extended by a further section turning in existing Bramford - Rayleigh/Braintree, Pelham - Sizewell and Norwich - Sizewell 400kV circuits. | EDF Energy Nuclear Generation Ltd | Sizewell North 400kV Substation | Sizewell C | 31/10/2019
|  | East Anglia FOUR Limited | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | East Anglia 4 | 01/04/2027
|  | East Anglia THREE Limited | Platform EA3A and Platform EA3B 220/33kV Substations | East Anglia 3
20551 | 1. Thermal uprate of the Aberthaw – Tremorfa circuit 2. Thermal uprate of the circuits from Whitson – Iron Acton – Melksham 3. Thermal uprate of the Imperial Park – Melksham and the Cilfynydd – Whitson – Seabank circuit (Severn Cable circuits) 4. Thermal uprate of the Cowley – Walham circuit 5. Thermal uprate of the Cardiff East – Uskmouth – Whitson circuit 6. Thermal uprate of the Cardiff East leg of the Pyle – Aberthaw – Cardiff East circuit 7. Thermal uprate of the Uskmouth – Whitson 2 circuit 8. Thermal uprate of Whitson SGT5 | Baglan Generating Ltd & Baglan Operations Ltd | Baglan Bay | Baglan Bay
20736 | Install a new 1100MVA 400/275kV transformer and bank this with the existing Swansea North SGT9 | Abernedd Power Company Ltd | Baglan Bay 275kV | Abernedd Power Station | 31/10/2026
20834-2 | Extend the above 400kV GIS substation at Bramford by a further 12 bays consisting of two further Sizewell bays, a further Norwich bay and two further bays for an additional Braintree/Rayleigh Main feeder bay and Pelham bay to be affected, together with four SGT bays to enable removal of the existing mesh substation at the site. An additional two bus couplers and one bus section complete the eventual 3 section substation design. | EDF Energy Nuclear Generation Ltd | Sizewell North 400kV Substation | Sizewell C | 31/10/2019
|  | East Anglia One Limited | Platform EA One 220/66kV Offshore Substation | East Anglia One | 03/01/2019
|  | East Anglia FOUR Limited | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | East Anglia 4 | 01/04/2027
|  | East Anglia THREE Limited | Platform EA3A and Platform EA3B 220/33kV Substations | East Anglia 3
|  | ScottishPower Renewables (UK) Limited | Platform EA2A and Platform EA2B 220/33kV Offshore Substations | East Anglia 2
|  | East Anglia FOUR Limited | Platform EA5A and Platform EA5B 220/33kV Substations | East Anglia 5
|  | East Anglia One Limited |  | East Anglia One North
20834-2A | Establish a new fully equipped GIS bay at Bramford 400kV substation interfacing with a 1200MW capacity OFTO circuit. | East Anglia One Limited | Platform EA One 220/66kV Offshore Substation | East Anglia One | 03/01/2019
|  | East Anglia THREE Limited | Platform EA3A and Platform EA3B 220/33kV Substations | East Anglia 3
|  | ScottishPower Renewables (UK) Limited | Platform EA2A and Platform EA2B 220/33kV Offshore Substations | East Anglia 2
|  | East Anglia One Limited |  | East Anglia One North
20834-3 | Install two switchable series reactors on the Tilbury and Coryton South feeder circuits at Rayleigh main. | East Anglia FOUR Limited | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | East Anglia 4 | 01/04/2027
|  | East Anglia FOUR Limited | Platform EA5A and Platform EA5B 220/33kV Substations | East Anglia 5
20900S | Construction of a new 400kV substation at close proximity to the company's existing Sealing End Compound at Aust on the 4YX route (Clifynydd - Whitson Seabank and Clifynydd - Imperial Park - Melksham). | Horizon Nuclear Power Oldbury Ltd | Oldbury-on-Severn 400kV Substation | Oldbury C | 01/06/2029
|  | Seabank Power Ltd | Seabank 400kV Substation | Seabank 3
20902L1 | Re-conductor 2VL Route. | Horizon Nuclear Power Oldbury Ltd | Oldbury-on-Severn 400kV Substation | Oldbury C | 01/06/2029
21348L | Create a new Seabank - Oldbury on Severn 400kV circuit and a new Oldbury on Severn - Melksham 400kV circuit. | Horizon Nuclear Power Oldbury Ltd | Oldbury-on-Severn 400kV Substation | Oldbury C | 01/06/2029
21348S | Oldbury on Severn substation works: two feeder bays, one bus coupler, two bus sections, one skeletal generator bay, one skeletal station transformer bay and system to generator intertrip scheme. | Horizon Nuclear Power Oldbury Ltd | Oldbury-on-Severn 400kV Substation | Oldbury C | 01/06/2029
21406S | Extension of 400kV busbars and substation building and installation of series reactor for generation connections at Killingholme substation. Extension to the existing South Humber Bank Operational Tripping Scheme. | Vi Aura Limited | Hornsea Platform 1C Offshore Substation | Hornsea Power Station 1C | 01/07/2020
|  | Heron Wind Ltd | Hornsea Platform 1A Offshore Substation | Hornsea Power Station 1A | 30/09/2019
|  | Njord Ltd | Hornsea Platform 1B Offshore Substation | Hornsea Power Station 1B | 28/02/2020
|  | Breesea Limited | Hornsea Platform 2A Offshore Substation | Hornsea Power Station 2A | 01/10/2020
|  | Breesea Limited | Hornsea Platform 2B Offshore Substation | Hornsea Power Station 2B | 01/04/2021
21406T1 | Bulk purchase of the series reactor at Killingholme 400kV Substation. | Vi Aura Limited | Hornsea Platform 1C Offshore Substation | Hornsea Power Station 1C | 01/07/2020
|  | Breesea Limited | Hornsea Power Station 2C Offshore platform | Hornsea Power Station 2C | 01/10/2021
|  | Heron Wind Ltd | Hornsea Platform 1A Offshore Substation | Hornsea Power Station 1A | 30/09/2019
|  | Njord Ltd | Hornsea Platform 1B Offshore Substation | Hornsea Power Station 1B | 28/02/2020
|  | Breesea Limited | Hornsea Platform 2A Offshore Substation | Hornsea Power Station 2A | 01/10/2020
|  | Breesea Limited | Hornsea Platform 2B Offshore Substation | Hornsea Power Station 2B | 01/04/2021
21619 - 11 | Associated substation works for the turn-in including the Penwortham and Daines feeder bays and GIB runs to connect the Penwortham - Daines circuit (ZQ route) to the new 400kV substation. | Wainstones Energy Ltd | Carrington 400kV | Trafford Power | 30/09/2018
21619 - 2 | OHL turn in the Penwortham - Daines circuit into existing Carrington substation. | Wainstones Energy Ltd | Carrington 400kV | Trafford Power | 30/09/2018
21619-1 | Extend the 400kV GIS double busbar substation at Carrington. | Wainstones Energy Ltd | Carrington 400kV | Trafford Power | 30/09/2018
21619-1S | Advance civil works at Carrington substation for Wainstones. | Wainstones Energy Ltd | Carrington 400kV | Trafford Power | 30/09/2018
21771 | Extend the 400kV AIS double busbar substation at Thorpe Marsh and all associated works. | Thorpe Marsh Power Ltd | Thorpe Marsh | Thorpe Marsh | 30/09/2020
21847 | Building a new double circuit overhead line between the Bramford, Twinstead Tee and Pelham substation strung with 3x 700mm2 AAAC conductor at 750C (28km), connecting into the new Bramford 400kV GIS substation. At Twinstead Tee rearrange the overhead line circuit to form the Bramford – Twinstead Tee -Pelham double circuit and Bramford – Twinstead Tee – Braintree – Rayleigh Main double circuit. | East Anglia FOUR Limited | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | East Anglia 4 | 01/04/2027
|  | East Anglia FOUR Limited | Platform EA5A and Platform EA5B 220/33kV Substations | East Anglia 5
30544SI | Extension of busbars at the Eastern end of Killingholme 400kV substation to accommodate a new OFTO bay for Hornsea P1. | Vi Aura Limited | Hornsea Platform 1C Offshore Substation | Hornsea Power Station 1C | 01/07/2020
|  | Heron Wind Ltd | Hornsea Platform 1A Offshore Substation | Hornsea Power Station 1A | 30/09/2019
|  | Njord Ltd | Hornsea Platform 1B Offshore Substation | Hornsea Power Station 1B | 28/02/2020
30637-1 | Build a new five bay 400kV AIS double busbar substation in the Lowestoft area, including two skeleton generator feeder bays, two feeder bays ad a bus coupler and additional works to enable the connection of 800MW. | East Anglia FOUR Limited | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | East Anglia 4 | 01/04/2027
30637-2 | Tee in the Norwich to Bramford circuit to the new Lowestoft substation. | East Anglia FOUR Limited | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | East Anglia 4 | 01/04/2027
30641-1 | Cable sealing end work for the new OHL. | East Anglia FOUR Limited | Platform EA4A and Platform EA4B 220/33kV Offshore Substations | East Anglia 4 | 01/04/2027
30648-1 | Establish two new feeder bays at Norwich 400kV substation for the connection of the new double circuit from Bacton. | East Anglia FOUR Limited | Platform EA6A and Platform EA6B and Platform EA6C 220/33kV Substations | East Anglia 6 | 01/04/2025
30752 | Build and install a South West Operational Tripping Scheme (OTS) | Aquind Limited | Lovedean 400kV Substation | Aquind Interconnector | 01/10/2020
31198 | Extension of 400kV busbars and installation of bus section breakers and bus coupler for generation connections at the Western side of Killingholme 400kV Substation. | Breesea Limited | Hornsea Power Station 2C Offshore platform | Hornsea Power Station 2C | 01/10/2021
|  | Breesea Limited | Hornsea Platform 2A Offshore Substation | Hornsea Power Station 2A | 01/10/2020
|  | Breesea Limited | Hornsea Platform 2B Offshore Substation | Hornsea Power Station 2B | 01/04/2021
31671-1 | Re-conductoring Bramley - Fleet 1&2 circuits | Aquind Limited | Lovedean 400kV Substation | Aquind Interconnector | 01/10/2020
31671-2 | Re-conductoring Fleet - Lovedean 1&2 circuits | Aquind Limited | Lovedean 400kV Substation | Aquind Interconnector | 01/10/2020
31832-3 | Thermal reinforcement to the South Coast | Aquind Limited | Lovedean 400kV Substation | Aquind Interconnector | 01/10/2020
31868L | Single turn-in into the new Knottingley 400 kV substation the Eggborough – Ferrybridge to form an Eggborough – Knottingley and Ferrybridge – Knottingley circuit connection | Knottingley Power Limited | Knottingley | Knottingley Power Station | 30/09/2019
31868S | Construct a new 5 bay Knottingley 400 kV GIS substation (two skeletal generator bays, two feeder bays and one bus coupler bay), associated new LVAC protection and control works. Installation of a local Operational Tripping Scheme in accordance with Appendix F3 of the Bilateral Connection Agreement | Knottingley Power Limited | Knottingley | Knottingley Power Station | 30/09/2019
31926S | Scheme Description Extend main bar 2 and south side of reserve Bar 2 at Keadby 400kV substation to provide one skeleton bay at the busbar extension. Extend main bar 2 and south side of reserve Bar 2 at Keadby 400kV substation to provide one skeleton bay at the busbar extension. | Keadby Generation Ltd | Keadby | Keadby II | 01/04/2021
32311O | Move SVC 5 isolator/disconnectors and extend substation busbars to the West to provide a skeletal bay to connect the HVDC interconnector. | FABLink Ltd | Exeter 400KV Substation | FAB Link Interconnector | 01/12/2020
32311SI | Extend the substation busbar to the East to provide a skeletal bay to connect the HVDC interconnector. | FABLink Ltd | Exeter 400KV Substation | FAB Link Interconnector | 01/12/2020
32313SI | Uprate the existing switchgear at Margam 275kV substation. Replace circuit breaker 2T0 at Margam 66kV substation | Abernedd Power Company Ltd | Baglan Bay 275kV | Abernedd Power Station | 31/10/2026
32339LI | Build a new double circuit from the new Bacton 400kV substation to the existing Norwich 400kV substation. | East Anglia FOUR Limited | Platform EA6A and Platform EA6B and Platform EA6C 220/33kV Substations | East Anglia 6 | 01/04/2025
32339SI | Build 400kV AIS double busbar substation in the Bacton area, including one skeleton generator bay, two feeder bays and a bus coupler and additional works to connect 600MW. | East Anglia FOUR Limited | Platform EA6A and Platform EA6B and Platform EA6C 220/33kV Substations | East Anglia 6 | 01/04/2025
32452 | Extension of the existing Norwich Main 400 kV substation to accommodate the connection of 2 skeletal bays, a new busbar coupler circuit breaker bay and a new reserve busbar section circuit breaker bay. Extension of the existing East Anglia Operational Tripping Scheme in accordance with Appendix F3 of the Bilateral Connection Agreement. | SMart Wind SPC5 Limited | Hornsea Platform 3A Offshore Substation | Hornsea Power Station 3A | 01/04/2023
|  | SMart Wind SPC6 Limited | Hornsea Platform 3B Offshore Substation | Hornsea Power Station 3B | 01/10/2023
|  | SMart Wind SPC7 Limited | Hornsea Platform 3C Offshore Substation | Hornsea Power Station 3C (Formally 4A) | 01/04/2024
|  | SMart Wind SPC8 Limited | Hornsea Platform 3D Offshore Substation | Hornsea Power Station 3D (formally 4B) | 01/10/2024
32641SI | uprate circuit breakers at Carrington 400kv | NuGeneration Ltd | Moorside 400kV Substation | Moorside
32642SI | uprate circuit breakers at Daines 400kv | NuGeneration Ltd | Moorside 400kV Substation | Moorside
32643SI | uprate circuit breakers at Harker 275kv | NuGeneration Ltd | Moorside 400kV Substation | Moorside
32644SI | Uprate circuit breakers at Kearsley 275kv substation | NuGeneration Ltd | Moorside 400kV Substation | Moorside
32645SI | Uprate circuit breakers at Fiddlers Ferry 275kv | NuGeneration Ltd | Moorside 400kV Substation | Moorside
32647LI | Reconductor Carr | NuGeneration Ltd | Moorside 400kV Substation | Moorside
32906 | Circuit diversion at Eggborough 400 kV substation to connect together the Monk Fryston 1 and Drax 2 Circuits such that they no longer connect in to Eggborough 400 kV substation. Install an additional SGT at Monk Fryston 275kV substation and up rate the Drax - Monk Fryston circuit to match the new rating. | Knottingley Power Limited | Knottingley | Knottingley Power Station | 30/09/2019
33237I | Provision of the skeletal bay for the User to connect. The existing SGT1 skeletal bay assets are to be transferred to the User. | J G Pears Grid Connection Ltd | High Marnham | J G Pears | 08/04/2018
33285 | Re-conductor the Carrington to Daines 4 circuit (~2km) with 2 x 620mm² GZTACSR gap-type conductor at 170°C. | Wainstones Energy Ltd | Carrington 400kV | Trafford Power | 30/09/2018
33285L | Rephasing of the Carrington - Penwortham circuit. | Wainstones Energy Ltd | Carrington 400kV | Trafford Power | 30/09/2018
33285O | Build one skeletal GIS bays for connection of the generation. | Wainstones Energy Ltd | Carrington 400kV | Trafford Power | 30/09/2018
33285S | Scheme Description Build and install a Category 1 intertrip to trip the generation for faults which overload the NETS and also two skeletal GIS bays for connection of the generation. Build and install a Category 1 intertrip to trip the generation for faults which overload the NETS and also two skeletal GIS bays for connection of the generation. | Wainstones Energy Ltd | Carrington 400kV | Trafford Power | 30/09/2018
33730 | Extend the existing Baglan Bay 275kV substation to accommodate a new GIS generator bay. Install a generator to system intertrip scheme. Uprate the existing switchgear at Pyle 275kV substation | Abernedd Power Company Ltd | Baglan Bay 275kV | Abernedd Power Station | 31/10/2026
33748 | Kinsnorth Works, including: - Provide the customer with a spare bay at Kingsnorth 400kV substation (spare bay 3). - Kingsnorth circuit breaker foundation (Xl 05, Xli 0, X140, X205, X21 0 X705 X805 and X1090) updating works - Installation of a new coupler breaker with associated bay works between main busbar 3 and circuit breaker X220. | Gridlink Interconnector Ltd | Kingsnorth | Gridlink Interconnector | 31/10/2022
33793 | • Extension of Pembroke 400kV substation to accommodate one new GIS generator bay, including busbar protection and SCS update • Installation of a generator to system intertripping scheme (thermal and stability) • Replacement of feeder circuit breakers of Pembroke – Swansea North #1 and #3 and modification of feeder protection • Thermal uprate of the Whitson leg of Tremorfa - Uskmouth – Whitson circuit • Replacement of the Cowley – Walham cables • Thermal uprate of Imperial Park – Melksham and Cilfynydd – Whitson – Seabank circuits • Thermal uprate of the Iron Acton – Melksham circuits 1 and 2 • Thermal uprate of Iron Acton – Whitson circuits 1 and 2 • Remove the Quad boosters 1 and 2 at Whitson • Replacement of Whitson SGT5 for a larger rated unit • Thermal uprate of the Cardiff East – Uskmouth – Whitson (Cardiff East leg) • Thermal uprate of the Cardiff East – Uskmouth – Whitson (Whitson leg) • Thermal uprate of the Aberthaw – Tremorfa circuit. • Thermal uprate of the Cardiff East leg of the Pyle – Aberthaw – Cardiff East circuit | Egnedol Pembroke Eco-Power Ltd |  | Milford Haven | 31/10/2026
Aberarder item 1 | Establishment of approx. 5km of new single circuit 132kV wood pole trident line between the proposed wind farm substation at Aberarder and the Dunmaglass-Farigaig 132kV overhead line circuit. At Aberarder wind farm substation, the 132kV overhead circuit will terminate on to a new 132kV circuit switcher (115) to be established within the substation compound. At Dunmaglass - Farigaig side the overhead line circuit will terminate via a 132kV circuit switcher (125) to be established within a switching compound to be established adjacent to the existing Dunmaglass-Farigaig overhead line. The circuit switcher 125 will tee into the Dunmaglass-Farigaig circuit at this point. | Aberarder Wind Farm LLP | Aberarder 132/33Kv Substation | Aberarder Wind Farm | 30/06/2020
Achlachan Item 1 | At Mybster 132/33kV substation, the Relevant Transmission Licensee shall replace the existing 2 x 30 MVA and 1 x 60 MVA 132/33kV transformers with higher rated twin 120MVA 132/33kV transformers within the same substation accommodation. The works will include all associated plinth foundations, transformer protection equipment, and 33kV cabling work associated with the two replacement 120MVA transformers. | Achlachan Wind Farm LLP |  | Achlachan
Achlachan Item 12 | The User has requested non-firm access ahead of completion of the required transmission enabling works, SHET-RI-058 and SHETL-RI-060. This will require the implementation of an Intertrip scheme to disconnect the output of the windfarm from the network via the relevant circuit breaker, when the new HVDC link between Spittal substation (Caithness) and Blackhillock substation (Morayshire) is unavailable. These works therefore cover the design, installation and commissioning of a temporary Intertrip scheme to give access to the transmission system by the User’s agreed connection date of 31st October 2018. | Achlachan Wind Farm LLP |  | Achlachan
Achlachan Item 2 | Install 2 x 132kV transformer circuit breaker bays connected off the Mybster 132kV busbar extension, complete with protection and associated auxiliary equipment. (The incumbent 33kV switchboard and 132kV transformer circuit switchers are adequately rated to meet the 120MVA transformer capacity; hence no further works are required) | Achlachan Wind Farm LLP |  | Achlachan
Achlachan Item 3 | Install 2 x 33kV busbar disconnector switches connected off the new double 33kV busbar at the Relevant Transmission Licensee’s 132 / 33kV substation within the extended Mybster compound | Achlachan Wind Farm LLP |  | Achlachan
Annabaglish item 1 | At Glenluce 132kV substation installation of two new 132kV line isolators on the GT1B and GT2B transformers and two transformer 33kV circuit breakers, to form a second 33kV switchboard (B Board). Installation of all associated 33kV cabling to connect the Grid T1B and T2B transformers to the 33kV circuit breakers. | RES UK & Ireland Limited | Glenluce 132/33kV | Annabaglish | 31/10/2023
Annabaglish item 2 | At Glenluce 132kV substation, installation of two new 132kV line insolators on the GT1B and GT2B transformers, associated 132kV cablings and associated equipment. | RES UK & Ireland Limited | Glenluce 132/33kV | Annabaglish | 31/10/2023
Ardtaraig Item 1 | At Dunoon 132/33kV Grid Supply Point substation, replace the existing 2 x 45MVA 132/33kV grid transformers with 2 x 90MVA 132/33kV transformers. Upgrade the two 33kV transformer incomer breakers (1T0 and 2T0) and the corresponding Isolators (1T7 and 2T7) to accommodate the additional capacity. Undertake upgrades to the existing transformer plinths and foundations to accommodate the larger transformers. Connect the new 33kV transformer incomer breakers/isolators via suitably rated 33kV cabling to the new 90MVA units. As a result of the requirement to upgrade the existing 2 x 45MVA grid transformers a termination fee will be payable in respect of the asset removed prior to the end of its economic life. | Infinergy Ltd |  | Ardtaraig Wind Farm | 31/10/2021
Bad A Cheo Part 1 | Install 2 x 33kV busbar disconnector switches connected off the new double 33kV busbar at the relevant transmission licensee's 132/33kV substation with the extended Mybster compound. | Innogy Renewables UK Ltd | Mybster 132/33kV | Bad a Cheo Wind Farm
Beaw Field item 1 | The connection will be provided by a transmission 132kV circuit from the new 132kV double busbar at Kergord substation. The 132kV circuit will consist of the following: (a) 20km of 132kV wood pole overhead line between Kergord and Mossbank on the northern shore of the main island. (b) 4km of 132kV subsea cabling between Mossbank (main island) and the Bay of Ulsta (on Yell). (c ) 6km of 132kV wood pole overhead line between the Bay of Ulsta and the Beaw Field wind farm development site on the isle of Yell. At the wind farm substation, the 132kV wood pole overhead line through Yell will terminate on a 132kV transformer circuit switcher 115 located at the wind farm 132/33kV substation compound. In addition, (i) install 2 x 132kV busbar selector disconnectors, along with associated busbar extensions and support structures within Kergord 132kV substation compound. (ii) Install 1 x 132kV line circuit breaker along with associated line disconnector at Kergord 132kV substation compound. (iii) Install 1 x 132kV transformer circuit switcher within the wind farm substation compound. (iv) Modify the existing protection and telecommunication equipment at Kergord 132kV substation to suit the new connection at Beaw Field. | Peel (Yell) Wind Farms Limited | Yell | Beaw Field Wind Farm
Beinn An Tuirc III item 1 | At Carradale 132kV substation establish a new 1 x 132kV wind farm feeder circuit breaker (435) to be coupled to the RC2 circuit side of the existing 132kV Carradale - Crossaig double circuit tower line (RC1/RC2) within the existing Carradale 132/33kV Grid Supply Point substation compound. The 1 x 132kV circuit breaker shall be configured as a wind farm feeder unit and shall be coupled to the Beinn An Tuirc III wind farm overhead line circuit. Establish approx. 12km of new 132kV single circuit overhead wood pole trident circuit between Carradale 132kV substation compound and the Beinn An Tuirc III wind farm development. At Carradale the new overhead line circuit will be coupled to the new 1 x 132kV wind farm circuit breaker (435). At Beinn An Tuirc III the overhead line will terminate on to a new 132kV circuit switcher (115) to be installed within the Beinn An Tuirc III wind farm substation compound. The high voltage side of the wind farm substation transformer will be coupled to the new circuit switcher (115). Modify the existing protection and telecommunication schemes at Carradale and Crossaig substation to facilitate the connection of the new 132kV wind farm feeder circuit as required. | ScottishPower Renewables (UK) Limited | Carradale 132/33kV Substation | Beinn an Tuirc 3
| The works include installation of a new 132kV feeder circuit breaker at the existing Dyce 132kV substation, complete with 132kV busbar disconnector and 132kV line circuit breaker. The works at the existing Dyce 132kV substation also include the installation of 132kV transformer circuit switcher on the existing grid transformer GT1. | Aberdeen Offshore Wind Farm Limited | Blackdog 132kV Substation | Aberdeen Offshore Wind Farm | 01/04/2018
| The replacement of section tower near the tail end of double circuit tower line (XPN/XPS) at Stoneyhill and the installation of 9.5km of 132kV underground cable from 132kV circuit XPS at Stoneyhill to the new 132kV substation building at the user's landfall site. At the landfall substation, the 132kV substation building at the user's landfall site. At the landfall substation, the 132kV underground cable will terminate onto a 132kV GIS line disconnector located within the substation building. The cabling will comprise three single core XLPE Cu 630mm cables to meet the wind farm capacity. | Aberdeen Offshore Wind Farm Limited | Blackdog 132kV Substation | Aberdeen Offshore Wind Farm | 01/04/2018
| Modification of existing protection and telecommunications equipment at Kintore and Dyce 132kV substations to suit the new Aberdeen Offshore connection arrangement. | Aberdeen Offshore Wind Farm Limited | Blackdog 132kV Substation | Aberdeen Offshore Wind Farm | 01/04/2018
| The relevant transmission licensee will connect downdropper conductors between tower 34 of the Keither/Macduff single 132kV line and the adjacent terminal wood pole on the new trident 132kV line to the windfarm. | Vattenfall Wind Power Ltd | Aultmore 132/33kV | Aultmore Wind Farm | 01/07/2018
| The relevant transmission licensee will also install or modify (as applicable) intertripping arrangements between the Keith substations, Macduff substation and the wind farm substations. | Vattenfall Wind Power Ltd | Aultmore 132/33kV | Aultmore Wind Farm | 01/07/2018
| Installation of a 132kV line circuit breaker at Magree Substation and from this point construction of a 132kV single circuit overhead line Blackcraig wind farm terminating at a 132kV isolator at Blackcraig Wind farm site. | Blackcraig Wind Farm (Scotland) Limited | Black Craig | Blackcraig Wind Farm
| Provision of equipment to receive communications, alarms, indications and metering. | Blackcraig Wind Farm (Scotland) Limited | Black Craig | Blackcraig Wind Farm
| Thermal overload relief work. | South Eastern Power Networks |  | Canterbury North
|  | South Eastern Power Networks |  | Bolney
| The relevant transmission licensee will install a single 132kV circuit rated at a minimum of 180MVA, comprising approximately 10km of underground cable and 20km of subsea cable, between Cantick Head and South Ronaldsay 132kV substations. There will be two 132kV circuit switchers at Cantick Head substation and a fully equipped feeder bay at South Ronaldsay 132kV substation. | Brims Tidal Array Limited | Bay of Skaill 132/33kV substation | Cantick Head
| Reconfiguration of busbar at Mawwick Head substation to connect AC circuit to the section of the busbar with the HVDC link. | Brims Tidal Array Limited | Bay of Skaill 132/33kV substation | Cantick Head
| Installation of approximately 1km of 132kV overhead line between Chirmorie wind farm substation and the tee point on the Mark Hill to Stranoch wind farm overhead line. | Chirmorie Wind Farm Limited |  | Chirmorie Wind Farm | 31/10/2022
| Installation of a 132kV line isolator at Stranoch wind farm substation. | Chirmorie Wind Farm Limited |  | Chirmorie Wind Farm | 31/10/2022
| Construction of approximately 10km of double circuit 400kV steel tower line and 2km 400kV cable from Invergarry to the connection site. | SSE Generation Ltd | Coire Glas | Coire Glas Pumped Storage | 31/10/2025
| Installation of 400kV GIS double busbar arrangement and associated bus section circuit breakers/isolators at the connection site. | SSE Generation Ltd | Coire Glas | Coire Glas Pumped Storage | 31/10/2025
| Establish a 132kV substation at the Coalburn North 132kV substation. | 3R Energy Solutions | Coalburn132/33kV | Douglas West | 31/10/2021
| Install a 132kV line disconnector and 132kV busbar. | 3R Energy Solutions | Coalburn132/33kV | Douglas West | 31/10/2021
| Install 0.1km of 2000mm² Cu XLPE cable to loop in to the cable section of the Coalburn - Linnmill No.1 132kV circuit. | 3R Energy Solutions | Coalburn132/33kV | Douglas West | 31/10/2021
| Establishment and installation of two 132kV line isolators at Dunbar GSP. | Viridor Enviroscot Limited | Dunbar | Dunbar ERF | 31/10/2021
| Extend the existing Eaton Socon 400kV substation to provide for a new 400kV SGT3 bay and 400/132kV 240MVA transformer. | Eastern Power Networks |  | Eaton Socon
| The establishment of a new 132/33kV substation compound at Elchies including all substation internal civil works, including plinth foundations, bases, access roadway and control/switchroom. The substation will be located approximately 7km north of Aberlour. The company reserves the right to revise this construction agreement and the relevant bilateral connection agreement upon advise from the relevant transmission licensee should the ground conditions require excessive and/or protracted civil works and additional infrastructure. | Elchies Wind Limited | Elchies 132/33kV Substation | Elchies Wind Farm
| Install a 7km 132kV wood pole trident line between Aberlour 275/132kV substation and the new 132/33kV substation facility at Elchie with the line terminated on the new 132kV switchgear installed at both substation ends. The 132kV wood pole line will be strung with 3 wire 175mm ACSR conductors, with a conductor operating temperature of 75°C, to meet the windfarm capacity. | Elchies Wind Limited | Elchies 132/33kV Substation | Elchies Wind Farm
| At Aberlour 275/132kV substation, install a 132kV feeder circuit breaker bay connected off the substation double 132kV busbars, complete with plinths/foundation, support structures, post insulators, busbars, line disconnector and associated protection, control and metering equipment. | Elchies Wind Limited | Elchies 132/33kV Substation | Elchies Wind Farm
| At the Elchies 132/33kV substation a new 132kV line disconnector and associated earth switch. | Elchies Wind Limited | Elchies 132/33kV Substation | Elchies Wind Farm
| Extend the Tealing 275kV busbar to accommodate one feeder bay and one bus coupler. Upgrade the Tealing 275kV busbar to 4000A rating. Install 1 x 275kV fully equipped feeder bay, 1 x 275kV fully equipped bus coupler bay at Tealing 275kV substation and energy metering. | Seagreen Wind Energy Ltd | Tealing 275/33kv | Firth of Forth Offshore Wind Farm 1A | 30/06/2019
|  | Seagreen Wind Energy Ltd | Tealing 275/33kv | Firth of Forth Offshore Wind Farm 1B | 30/06/2019
| Completion of all associated protection and control works. | Seagreen Wind Energy Ltd |  | Firth of Forth Offshore Wind Farm 2A East & 2A West
|  | Seagreen Wind Energy Ltd | Branxton 400kV | Firth of Forth Offshore Wind Farm 2B East & 2B West
|  | Neart Na Gaoithe Offshore Wind Ltd |  | Neart Na Gaoithe Offshore Wind Farm
| All associated miscellaneous and minor works, including provision of Category 2 intertripping scheme and Category 4 intertripping scheme, as defined in the Grid code. | Seagreen Wind Energy Ltd |  | Firth of Forth Offshore Wind Farm 2A East & 2A West
|  | Seagreen Wind Energy Ltd | Branxton 400kV | Firth of Forth Offshore Wind Farm 2B East & 2B West
|  | Neart Na Gaoithe Offshore Wind Ltd |  | Neart Na Gaoithe Offshore Wind Farm
| Installation of 400kV plant and apparatus at Branxton 400kV substation which will form the connections to the two 2B East and 2B West transmission interface points, including busbars, circuit breakers, disconnectors, earth switches, current and voltage transformers. | Seagreen Wind Energy Ltd |  | Firth of Forth Offshore Wind Farm 2A East & 2A West
|  | Seagreen Wind Energy Ltd | Branxton 400kV | Firth of Forth Offshore Wind Farm 2B East & 2B West
| Installation of two new 132/33kV 90MVA transformer units (Grid T1 and T2) and all associated cablings to connect the transformers to Grid T1 and Grid T2 33kV circuit breakers on the Newton Stewart 33kV switchboard. | Willowind Gass Limited | Newton Stewart | Gass Wind Farm | 30/10/2023
| Installation of one 132kV switchbay, three 1 line isolators and associated 132kV underground cables for interconnections and terminations at Newton Stewart 132kV substation. | Willowind Gass Limited | Newton Stewart | Gass Wind Farm | 30/10/2023
| Modify the tower near the new 132/33kV windfarm substation and erect a new terminal tower and down droppers to the new substation compound. | Kilmac Energy | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm
| Install 2 x 132kV line isolating switches (103 and 203) along with associated busbar extensions and support structures within the substation compound. Isolators to be located on either side of the single teed 132kV infeed to the substation. | Kilmac Energy | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm
| Install 1 x 132kV transformer circuit breaker (115) along with associated busbar extensions and support structures. | Kilmac Energy | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm
| Modify the existing protection and telecommunication equipment's at Fort Augustus and the new 132kV substation near Dunvegan. | Kilmac Energy | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm
| At Neilston 132kV substation, provide 132kV busbar connection, associated civil works and ancillary equipment | Gamesa Energy UK Ltd | Glenouther 132/33kV Substation | Glenouther Wind Farm (Harelaw) | 30/05/2020
| Installation of one 132kV line isolator at Kype Muir Wind Farm substation. | Banks Renewables (Harting Rig Wind Farm) Limited | Harting Rig 132/33kv | Harting Rig Wind Farm | 30/07/2020
| Build a new 400kV GIS double busbar substation. | National Grid International Ltd | Chilling 400KV Substation | IFA2 Interconnector | 31/10/2019
| Install six new GIS Bays which are for four feeder circuits, one bus coupler and one shunt reactor. | National Grid International Ltd | Chilling 400KV Substation | IFA2 Interconnector | 31/10/2019
| Provision for the User to install their GIS bay. | National Grid International Ltd | Chilling 400KV Substation | IFA2 Interconnector | 31/10/2019
| Extend and uprate the Main and Reserve busbars at Cockenzie 275kV substation as required. | Inch Cape Offshore Ltd | Cockenzie 275kV | Inch Cape Offshore Wind Farm Platform 1 | 01/04/2018
|  | Inch Cape Offshore Ltd | Cockenzie 275kV | Inch Cape Offshore Wind Farm Platform 2 | 30/04/2020
| Install a new 275kV switchbay at Cockenzie 275kV substation and associated equipment and apparatus to the Interface point. | Inch Cape Offshore Ltd | Cockenzie 275kV | Inch Cape Offshore Wind Farm Platform 1 | 01/04/2018
|  | Inch Cape Offshore Ltd | Cockenzie 275kV | Inch Cape Offshore Wind Farm Platform 2 | 30/04/2020
| Provide communications, alarms, indications and metering. | Inch Cape Offshore Ltd | Cockenzie 275kV | Inch Cape Offshore Wind Farm Platform 1 | 01/04/2018
|  | Inch Cape Offshore Ltd | Cockenzie 275kV | Inch Cape Offshore Wind Farm Platform 2 | 30/04/2020
|  | Neart Na Gaoithe Offshore Wind Ltd |  | Neart Na Gaoithe Offshore Wind Farm
| New bay including one 132kV circuit breaker and all associated equipment and apparatus for the connection of the Kennoxhead wind farm circuit. | Brookfield Renewable UK Ltd | Kennoxhead | Kennoxhead Wind Farm | 31/10/2023
| Installation of approximately 0.3km 132kV underground cable and 17km of 132kV single circuit wooden pole overhead line with 200mm² conductor between Coalburn 132kV substation and Kennoxhead wind farm connection substation. | Brookfield Renewable UK Ltd | Kennoxhead | Kennoxhead Wind Farm | 31/10/2023
| Installation of one 132kV line isolator at Kennoxhead wind farm connection substation. | Brookfield Renewable UK Ltd | Kennoxhead | Kennoxhead Wind Farm | 31/10/2023
| Install a new 275kV switchbay at Mark Hill 275kV substation. | ScottishPower Renewables (UK) Limited | Kilgallioch 132/33kV Substation | Kilgallioch
| Establish a 275kV substation at the Kilgallioch wind farm site and install a 275kV line isolator and all the relevant transmission licensees protection/telecommunications apparatus required at the relevant transmission licensees Kilgallioch substation. | ScottishPower Renewables (UK) Limited | Kilgallioch 132/33kV Substation | Kilgallioch
| Installation of one 132kV line isolator at Kype Muir wind farm collector substation. | Banks Renewables Limited | Coalburn 132/33kV | Kype Muir | 17/09/2018
| Installation of a new bay including one 132kV circuit breaker and all associated equipment apparatus at Coalburn 132kV substation for the connection of Middle Muir wind farm circuit. | Banks Renewables Limited | Middle Muir 132/33kV | Middle Muir Wind Farm | 30/05/2018
| Installation of one 132kV line isolator at Middle Muir wind farm connection substation. | Banks Renewables Limited | Middle Muir 132/33kV | Middle Muir Wind Farm | 30/05/2018
| Installation of Operational tripping scheme. | NuGeneration Ltd | Moorside 400kV Substation | Moorside
| Extension of the existing Crystal Rigs 400kV substation and the installation of 400kV plant and apparatus which will form the connections to the two Transmission Interface Points, including busbars, circuit breakers, disconnectors, earth switches, surge arresters, current and voltage transformers. | Neart Na Gaoithe Offshore Wind Ltd |  | Neart Na Gaoithe Offshore Wind Farm
| Modification of the existing bus coupler and associated plant and apparatus at Crystal Rig 400kV substation, including relocation of the existing 400kV circuit breaker X130. | Neart Na Gaoithe Offshore Wind Ltd |  | Neart Na Gaoithe Offshore Wind Farm
| Erect a single 132kV wood pole line over a distance of approximately 6km between the 132/33kV substation facility at the Glenmorie windfarm development site and the new Relevant transmission licensee's 275/132kV substation at Fyrish. The 132kV line will be built using portal wood pole 'H' type construction, and stung with 150mm ACSR conductors to meet the Windfarms connection capacity. Some minor circuit under grounding maybe required along the final circuit route. | WKN Sallachy Ltd | Sallachy 132kV Substation | Sallachy Wind Farm
| At Cassley 132/33kV substation install a 132kV feeder circuit breaker bay and connected off the incoming 132kV line which terminates with the substation compound. The bay will include a single 132kV circuit breaker unit, a single 132kV line disconnector and associated busbar extension, support structure, protection, control and metering equipment. The incoming 132kV line circuit from Sallachy will terminate on support structures adjacent to the 132kV circuit breaker. | WKN Sallachy Ltd | Sallachy 132kV Substation | Sallachy Wind Farm
| Replace the Cassley 132kV transformer disconnector with a modern equivalent 132kV circuit switcher device. | WKN Sallachy Ltd | Sallachy 132kV Substation | Sallachy Wind Farm
| At the new Sallachy 132/33kV substation install a 132kV transformer circuit switcher. | WKN Sallachy Ltd | Sallachy 132kV Substation | Sallachy Wind Farm
| Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | Sandy Knowe Wind Farm Ltd | Glenglass 132/33kv | Sandy Knowe Wind Farm | 30/10/2021
|  | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV | Sanquhar II Wind Farm
| At Glenglass 132/33kV substation a new 132kV double switchbay (consisting of five line isolators and two circuit breakers owned by the relevant transmission licensee) and associated apparatus will be installed. | Sandy Knowe Wind Farm Ltd | Glenglass 132/33kv | Sandy Knowe Wind Farm | 30/10/2021
|  | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV | Sanquhar II Wind Farm
| At Carradale 132/33kV substation, the relevant transmission licensee shall replace the existing 2 x 60MVA 132/33kV transformers with higher rated 2 x 120MVA 132/33kV transformers within the same substation accommodation. The works include all associated plinth foundations, transformer protection equipment and cabling work associated with the installation of the replacement 120MVA 132/33kV transformers. The existing 132kV circuit switchers and associated 132kV cabling are adequately rated to meet the capacity of the new 120MVA 132/33kV transformers. However the existing 33kV transformer circuit breakers and associated 33kV cabling is not and will need to be replaced in order to meet the capacity of the new transformers. Minor modifications will require to be made to existing equipment to accommodate the larger transformer size, including earthing, fencing and substation equipment works. | SSE Renewables Developments (UK) Ltd | Carradale | Tangy III Wind Farm | 01/04/2022
| At Coupar Angus Grid Supply Point substation replace the two 132/33kV 45MVA grid transformers with two higher rated 132/33kV 120MVA transformer units. Undertake upgrades to the existing transformer plinths and foundations to accommodate the larger transformers. Replace the two existing 33kV 1250 amp outdoor transformer circuit breakers with two higher rated 33kV 2500 amp transformer incomer breakers. | Tullymurdoch Limited | Coupar Angus | Tullymurdoch Wind Farm | 30/11/2016
| Construction of a 132kV double tee at Whiteside Hill 'T' point at the Whiteside Hill 132/33kV substation. | Whiteside Hill Windfarm (Scotland) Limited | Coylton | Whiteside Hill Wind Farm
| Establish a 132kV substation compound at the Whiteside Hill 132/33kV substation site along with 2 x 30MVA 132/33kV transformers with associated switchgear. | Whiteside Hill Windfarm (Scotland) Limited | Coylton | Whiteside Hill Wind Farm
| Establish a control/switchroom containing a 33kV double busbar switchboard and all protection/telecommunications apparatus required at the Whiteside Hill Substation site. | Whiteside Hill Windfarm (Scotland) Limited | Coylton | Whiteside Hill Wind Farm
| Provide two new tee circuits by banking them with outgoing feeders from 2 existing kV circuit breakers (Acton Lane GT1 & GT2 circuits) including GIS disconnector on each circuit. | Scottish & Southern Electricity Power Distribution |  | Willesden
| Replace a short section of cable circuit of each of GT1 and GT2. | Scottish & Southern Electricity Power Distribution |  | Willesden
Blary Hill item 5 | At Carradale 132/33kV substation The Relevant Transmission Licensee shall replace the existing 2 x 60MVA 132/33kV transformers with higher rated 2 x 120MVA 132/33kV transformers within the same substation accommodation. The works include all associated plinth foundations, transformer protection equipment and cabling work associated with the installation of the replacement 120MVA 132/33kV Transformers. The incumbent 132kV circuit switchers and associated 132kV cabling are adequately rated to meet the capacity of the new 120MVA 132/33kV transformers. However the existing 33kV transformer circuit breakers and associated 33kV cabling is not and will need to be replaced in order to meet the capacity of the new transformers. | RES UK & Ireland Limited | Carradale | Blary Hill Wind Farm
Creag Riabhach Item | At the new Dalchork 132/33kV grid substation install a new 132kV windfarm circuit breaker feeder bay complete with 2 x 132kV busbar selection switches, 1 x 132kV line disconnector and associated protection equipment. | Creag Riabhach Wind Farm Ltd | Creag Riabhach 132/33kV Substation | Creag Riabhach Wind Farm
Creag Riabhach item 1 | Install 18km of single circuit 132kV overhead wood pole trident line, strung with conductors to match the capacity of the wind farm, between Dalchork 132/33kV grid substation and the location of the User’s 132/33kV substation on site of the proposed wind farm. At the wind farm site install a new 132kV line disconnector and earth switch. | Creag Riabhach Wind Farm Ltd | Creag Riabhach 132/33kV Substation | Creag Riabhach Wind Farm
Creag Riabhach Item 2 | Connect the new 132kV overhead circuit from Dalchork 132/33kV grid substation to the Relevant Transmission Licensee’s 132kV metering circuit breaker installed within the User’s 132/33kV substation on site of the proposed wind farm. | Creag Riabhach Wind Farm Ltd | Creag Riabhach 132/33kV Substation | Creag Riabhach Wind Farm
Cumberhead Item 1 | Establish a 132kV substation at the Cumberhead Wind Farm site. | Cumberhead Wind Energy Limited | Cumberhead | Cumberhead | 20/10/2019
Cumberhead Item 2 | Installation of a 132kV line disconnector and 132kV busbar. | Cumberhead Wind Energy Limited | Cumberhead | Cumberhead | 20/10/2019
Cumberhead Item 3 | Install 0.4km of 1600mm2 Al XLPE cable to loop in to the Coalburn – Galawhistle Collector substation circuit. | Cumberhead Wind Energy Limited | Cumberhead | Cumberhead | 20/10/2019
Cumberhead Item 4 | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | Cumberhead Wind Energy Limited | Cumberhead | Cumberhead | 20/10/2019
Dorenell Wind Farm Part 1 | Part 1 – Enabling Works 1. Installation of 2 x 132kV Transformer circuit switchers and associated 132kV busbars at the new Dorenell 132/33kV substation. 2. Installation of 2 x 23km of 132kV overhead composite pole line between Dorenell wind farm132/33kV substation and the future upgraded Blackhillock 400/275/132kV substation. Each circuit shall be constructed using 300 sqmm UPAS conductor, with a conductor operating temperature of 75°C, to provide a minimum summer pre-fault rating of 176MVA. 3. At the future upgraded Blackhillock 400/275/132kV substation, install two 132kV feeder circuit breaker bays (for the two 132kV line circuits from Dorenell), complete with 2 x 132kV busbar disconnector switches, 1 x line disconnector, and associated 132kV protections on each bay. 4. Connect the new 2 x 132kV overhead line circuits from the Dorenell windFarm 132/33kV substation to the Relevant Transmission Licensee’s new 132kV circuit breaker bays at Blackhillock 400/275/132kV substation. | Dorenell Windfarm Limited | Dorenell 132/33kV | Dorenell Wind Farm | 01/04/2018
Druim leathann Item 1 | Installation of a single circuit 24km wood pole overhead circuit between the Druim Leathann windfarm and the proposed 132kV substation at Arnish, with one 132kV circuit switcher at Druim Leathann windfarm and a fully equipped 132kV feeder bay at Arnish 132kVsubstation. | Druim Leathann Windfarm Ltd | Druim Leathann 132/33kV substation | Druim Leathann | 31/12/2020
Enoch Hill Part 1 | 1. Extend the new 132kV substation compound at New Cumnock collector substation site location Grid Reference E251966, N608134 and install 1 x 132kV feeder bay. 2. Establish new 132/33kV substation compound at Enoch Hill Wind Farm site location, Grid Reference E255430,N608980 including the control /switch room 3. Installation of 0.25km of 132kV underground cable between New Cumnock and Enoch Hill Wind Farm substation. 4. Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | E.ON Climate & Renewables UK Developments Limited | Enoch Hill 132/33kV | Enoch Hill | 30/11/2020
Faw Side Item 1 | Establish a 132kV substation compound at Faw Side Community Wind Farm site. | Community Wind Power Ltd | Faw Side Community Wind Farm | Faw Side Community Wind Farm | 30/11/2024
Faw Side Item 2 | Install a 132kV line disconnector and 132kV busbar | Community Wind Power Ltd | Faw Side Community Wind Farm | Faw Side Community Wind Farm | 30/11/2024
Faw Side Item 3 | Install approximately 2.6km of 132kV wood pole overhead line (with a minimum summer pre-fault continuous rating of 222MVA) from Faw Side Community Wind Farm substation, to the Gretna to Hawick 132kV tower line (V Route) | Community Wind Power Ltd | Faw Side Community Wind Farm | Faw Side Community Wind Farm | 30/11/2024
Faw Side Item 4 | On V Route, install a junction tower to form a ‘T’ connection for the Faw Side Community Wind Farm 132kV circuit onto the Gretna to Hawick 132kv circuit. | Community Wind Power Ltd | Faw Side Community Wind Farm | Faw Side Community Wind Farm | 30/11/2024
Faw Side Item 5 | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of this Bilateral Connection Agreement | Community Wind Power Ltd | Faw Side Community Wind Farm | Faw Side Community Wind Farm | 30/11/2024
Faw Side Item 6 | Reinforce the Junction V to Harker 132kV circuit (from tower AL068 to Harker 132kV substation), to provide a minimum summer pre-fault continuous rating of 202MVA. | Community Wind Power Ltd | Faw Side Community Wind Farm | Faw Side Community Wind Farm | 30/11/2024
Glen Kyllachy Part 1 | Install a new 132 kV double busbar feeder bay comprising of 2 x132kV busbar selector disconnectors, 1 x 132kV line circuit breaker, 1 x 132kV line disconnector and associated protection and control equipment at Tomatin 275/132kV substation. The works also include establishment of a new 132kV single circuit connection between Tomatin 275/132kV substation and the Glen Kyllachy 132kV substation at the wind farm site. This will comprise of a 2.5km section of 132kV overhead wood pole trident line and a 0.5km section of underground 132kV cable circuit in order to facilitate entry into the proposed Tomatin 275/132kV substation compound. The new 132kV circuit will terminate into a new 132kV line disconnector installed at Glen Kyllachy 132kV substation. | Innogy Renewables UK Ltd | Glen Kyllachy Wind Farm | Glen Kyllachy Wind Farm | 28/08/2019
Glenmuckloch Hydro Pumped Storage Item 1 | Establish a 132kV substation at the Glenmuckloch Hydro Pumped Storage site | Glenmuckloch Pumped Storage Limite | Glenmuckloch 132kV Substation | Glenmuckloch Pumped Storage | 30/11/2022
Glenmuckloch Hydro Pumped Storage Item 2 | Install ~22km of 132kV overhead line incorporating a fibre optic cable (POPLAR, wooden pole) from Glenmuckloch 132kV substation to New Cumnock 132kV substation Board B | Glenmuckloch Pumped Storage Limite | Glenmuckloch 132kV Substation | Glenmuckloch Pumped Storage | 30/11/2022
Glenmuckloch Hydro Pumped Storage Item 3 | Install one new 132kV circuit breaker at New Cumnock Board B | Glenmuckloch Pumped Storage Limite | Glenmuckloch 132kV Substation | Glenmuckloch Pumped Storage | 30/11/2022
Golticlay Windfarm Part 1 | Establish a new 1 32kV Tee-off point on the future Loch Buidhe - Spittal 132kV double circuit OHL (currently known as MSW between Shin and Mybster), including any required tower modifications. Establish approximately 2.7km of new 132kV single circuit wood pole trident line between the new 132kV tee off point and Golticlay Wind Farm development. The 132kv wood pole trident circuit will terminate onto a new 132kV circuit switcher (115) to be installed within the Golticlay Wind Farm substation site compound. The 132kV circuit switcher (115) will be connected onto the high voltage terminals of the new 132/33kV Transformer unit. | E.ON Climate & Renewables UK Developments Limited | Golticlay 132/33kV | Golticlay Wind Farm | 31/10/2022
Harryburn Wind Farm Part 1 | Installation of a 132kV disconnector. | Innogy Renewables UK Ltd | Elvanfoot 275/132/33kV | Harryburn Wind Farm | 30/10/2020
Hopsrig Item 2 | Installation of one 1 32kV line Isolator at Hopsrig Wind Farm | Hopsrig Wind Farm Limited | Hopsrig Wind Farm 132/33kV Substation | Hopsrig Wind Farm | 30/10/2021
Hopsrig Item 3 | Installation of approximately 6.7km 132kV wood pole overhead line from Hopsrig wind farm to the Ewe Hill Collector Substation. | Hopsrig Wind Farm Limited | Hopsrig Wind Farm 132/33kV Substation | Hopsrig Wind Farm | 30/10/2021
Hopsrig Item 4 | Installation of a 132kV switchbay at Ewe Hill wind farm Collector Substation | Hopsrig Wind Farm Limited | Hopsrig Wind Farm 132/33kV Substation | Hopsrig Wind Farm | 30/10/2021
Limekilns Item 1 | Establishment of a new 132/33kV substation compound at Limekilns windfarm site including all substation internal civil works and the control/switchroom. | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
Limekilns Item 10 | Erect standard 132kV busbars and connect the 132kV busbars with the newly established 275kV busbars with SuperGridTransformers (SGT), which provides 240MW firm capacity. Each SGT is equipped with a 132kV circuit breaker and a 275kV circuit switch. The 132kV busbars are planned with attention for the future expansion for generation connections. | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
Limekilns Item 2 | Construction of a wood pole 132kV trident line over a distance of 4km between Dounreay substation the new Limekilns 132/33kV substation. The line will be strung with 3 wire 150mm ACSR conductors and profiled to allow a 75°C conductor operating temperature, in order to meet the windfarm connection capacity. The 132kV line circuit will be terminated to new 132kV switchgear installed at the substation ends. | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
Limekilns Item 3 | At Limekilns 132/33kV substation install a 132kV circuit breaker bay, complete with 132kV line disconnector and rated 132kV circuit breaker. | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
Limekilns Item 4 | At Dounreay substation, install an additional 132kV circuit breaker on the indoor 132kV switchboard. These works will include the following: (i) Install 1 x 132kv line Gas Insulated switch- Disconnector (603) along with associated support structures within the substation compound. (ii) Install 1 x 132kv line Gas Insulated switch- Disconnector (605) along with associated support structures within the substation compound station. (iii) Modify the existing protection and telecommunication equipments at Dounreay 275/132 kV substation. | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
Limekilns Item 9 | Identify, develop and construct a new 275kV/132kV substation north of Shin, along the existing MSE/W circuits erecting standard 275kV busbars within the compound. Connect the existing 275kV Beauly/Dounreay double circuits to the busbar, completed with circuit breakers. | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
Longburn Item 1 | Install a 132kV overhead line (~2km) between Longburn Wind Farm substation and the junction with the overhead line from Lorg Wind Farm. | Longburn Wind Farm Limited |  | Long Burn Wind Farm
Longburn Item 2 | Establish a 132kV substation at the Longburn Wind Farm substation with a 132kV line isolator and all protection/telecommunications apparatus required for the Relevant transmission Licensee. | Longburn Wind Farm Limited |  | Long Burn Wind Farm
Lorg Wind Farm PART 1 | 1. Installation of 132kV overhead line (~8km) between Lorg Wind Farm and the junction with the overhead line from Longburn Wind Farm. 2. Installation of one disconnector at Lorg Wind Farm. | E.ON Climate & Renewables UK Developments Limited | Lorg Wind Farm 132/32kV | Lorg Wind Farm | 15/11/2022
MeyGen Tidal Project item 1 | Install a double circuit 132kV overhead line with a summer pre fault capacity of 348MVA between Thurso South and a new 132kV GIS double busbar arrangement within a new substation facility at Gills Bay connecting in the two OHL radial circuits from Thurso south. | MeyGen Ltd | Gills Bay | MeyGen Tidal
Millennium South Item 1 | 1. The enabling works associated with the new 132/33kV substation adjacent to structure 39 of the Fort Augustus – Skye 132kV trident wood pole line (FQ1) will include the following: a. Modify structure 39 of the Fort Augustus – Skye 132kV trident wood pole line (FQ1) and erect a new terminal tower and down droppers to the new substation compound; b. Install 2 x 132kV line disconnectors (103 and 203) along with associated support structures within the substation compound. Disconnectors 103 and 203 to be located on either side of the single teed 132kV infeed to the substation. c. Install 1 x 132kV transformer circuit switcher (115), along with support structures within the substation compound. d. Provide a double 132kV tapping from either side of structure 39 to two new wood pole terminal structures located adjacent to the tower, and then extend two short trident lines over 3 – 5 spans to the new 132/33kV substation to establish a looped connection to the substation off the FFW circuit. e. Modify the existing protection and telecommunication equipment at Fort Augustus 132kV substation to suit the new teed connection at Millennium South. | Falck Renewables Wind Ltd | Millennium South 132/33kV Substation | Millennium South | 30/09/2016
Muaitheabhal Item 1 | The Relevant Transmission Licensee will install a 13km wood pole overhead line between Muaitheabhal Windfarm and the proposed 132kV switching station near Balallan (to be established under SHET-RI-043), with two 132kV circuit switchers at Muaitheabhal Windfarm and a 132kV circuit breaker at Balallan 132kV switching station. | EDF Energy Renewables Limited | Muaitheabhal 132/33kV Substation | Muaitheabhal Wind Farm
NGET-2GW | Install a 2GW HVDC converter station with associated equipment. HVDC cables to be routed into the sea and north towards Scotland. | NorthConnect KS | Peterhead 400KV | Norway Interconnector | 31/12/2022
NGET-32601SI | Extend the Rhigos 400kV substation busbar for the connection of Hirwaun Power Limited and one skeletal generator bay. Install two new feeder circuit bays for the turn-in of the Pembroke-Walham 400kV cable duck-under. Install one bus coupler bay. | Hirwaun Power Ltd | Rhigos | Hirwaun Power Station | 30/09/2020
NGET-RI- 32490LI | Replace existing set of cross-arms with modified set to allow tee-off into new sealing end compound. Install one set of down leads to gantries on Bramford - Sizewell 3 circuit, at tower 4ZX002. | Galloper Wind Farm Limited | Galloper North 132/33kv | Galloper Wind Farm | 01/01/2017
NGET-RI- 32490SI) | Supply and Install one GIS 132kV SGT bay, one AIS 400kV SGT bay and landing gantry for associated OHL tee connection works. Supply and Install two GIS 132kV skeletal bays, protection & control and associated civil works. Disconnection of Sizewell 132kV substation. | Galloper Wind Farm Limited | Galloper North 132/33kv | Galloper Wind Farm | 01/01/2017
NGET-RI-11076 | Reconductor Ironbridge - Rugely circuit with 2 x 570 AAAC conductors. | Organic Power Ltd | Connahs Quay 400kV | Marex
NGET-RI-11122 | Asset replacement of Walpole 132kV substation with a new GIS substation removing fault level restrictions currently precluding further 400kV and 132kV fault infeed at or near Walpole. | EP UK Power Developments Limited | Kings Lynn B 400kV Substation | Kings Lynn B | 31/10/2021
|  | DONG Energy RB (UK) Limited | Race Bank 132/33kV Substation | Race Bank Wind Farm
NGET-RI-11629 | Reconductor the Norwich - Walpole route (4VV) with 3 x 700mm² AAAC conductor operating at 75°C. | 3R Energy Solutions | Coalburn132/33kV | Douglas West | 31/10/2021
NGET-RI-11642 | Hotwiring of the Lovedean - Ninfield - Bolney circuits to increase their thermal rating. | South Eastern Power Networks |  | Ninefield
|  | South Eastern Power Networks |  | Canterbury North
|  | Seagreen Wind Energy Ltd | Tealing 275/33kv | Firth of Forth Offshore Wind Farm 1A | 30/06/2019
|  | South Eastern Power Networks |  | Bolney
NGET-RI-15080 | Reconductoring of the Cellarhead - Macclesfield 400kV circuit with 2 x 620mm² GAP conductor. | NuGeneration Ltd | Moorside 400kV Substation | Moorside
NGET-RI-20059 | To extend Walpole 400kV busbars for connection of two generator bays and to modify existing busbar protection to include the new generation. | DONG Energy RB (UK) Limited | Race Bank 132/33kV Substation | Race Bank Wind Farm
NGET-RI-20066IL | Connect Swansea North - Cilfynydd circuit into the new 400kV substation creating the Cilfynydd - Rhigos and Swansea North - Rhigos 400kV circuits. | Hirwaun Power Ltd | Rhigos | Hirwaun Power Station | 30/09/2020
|  | Greenwire Transmission Pembroke Limited | Pembroke 400kV Substation | Greenlink
NGET-RI-20066IS | Construct new Rhigos 400kV 4-bay double substation, comprised of a bus coupler circuit breaker, two feeder circuit breakers, a skeletal generation bay, a new control system and all protection. | Hirwaun Power Ltd | Rhigos | Hirwaun Power Station | 30/09/2020
|  | Greenwire Transmission Pembroke Limited | Pembroke 400kV Substation | Greenlink
NGET-RI-20488L | Install a new tower and line entries at Thorpe Marsh to connect the new substation in the Drax - Keadby - Brinsworth circuit. | Sargas Power Yorkshire Limited | Thorpe Marsh 400kV Substation | Hatfield Power Station | 30/09/2022
NGET-RI-20488S | Construct a new 400kV AIS double busbar substation at Thrope Marsh of 2 feeder bays, 1 generator bay and 1 bus coupler bay, on the site of the decommissioned part of the 275kV substation, extended to the North and West onto land currently owned by RWE Generation UK plc. | Thorpe Marsh Power Ltd | Thorpe Marsh | Thorpe Marsh | 30/09/2020
|  | Sargas Power Yorkshire Limited | Thorpe Marsh 400kV Substation | Hatfield Power Station | 30/09/2022
NGET-RI-20802-1 | Installation of a new 4 bay 400kV AIS double busbar substation at Bradwell consisting of two Rayleigh main feeder bays, one skeletal generator bay, one bus coupler bay and of the system-to-generator intertrip. | Bradwell Power Generation Company Limited | Bradwell 400kV Substation | Bradwell B
NGET-RI-20802-2 | Extension of the Rayleigh main double busbar 400kV AIS section by 2 bays to facilitate two new Bradwell 400kV feeder bays. | Bradwell Power Generation Company Limited | Bradwell 400kV Substation | Bradwell B
NGET-RI-20802-4 | Rayleigh main overhead line route using new design of tower and new foundations and strung with 2 x 570mm² AAAC conductor operating at up to 90°C. | Bradwell Power Generation Company Limited | Bradwell 400kV Substation | Bradwell B
NGET-RI-20832L | Decommissioning the 2 Bridgwater feeder bays at Hinkley Point 275kV substation and re-configure all 6 of the existing 400kV and 275kV feeder circuits at Hinkley Point to facilitate a new connection between Hinkley point and Seabank. | EDF Energy Nuclear Generation Ltd | Hinkley 400kV Substation | Hinkley Point C | 01/06/2022
NGET-RI-20832S | Installation of a new 18-bay 400kV GIS double busbar substation at Hinkley Point, consisting of eight feeder bays, two bus couplers, four bus sections, two skeletal generator bays and two skeletal station transformer bays. | EDF Energy Nuclear Generation Ltd | Hinkley 400kV Substation | Hinkley Point C | 01/06/2022
NGET-RI-20834-1 | Installation of two 400kV 3000MVA reactors in the existing Sizewell 400kV GIS substation site by utilizing and populating the four spare bays on the existing GIS originally identified for future nuclear generator station and unit transformer connections. | EDF Energy Nuclear Generation Ltd | Sizewell North 400kV Substation | Sizewell C | 31/10/2019
NGET-RI-20897L1 | Breaking into the existing Hinkley Point - Melksham OHL route near M5 motorway and teeing it into the Hinkley Point - Bridgwater circuit by a short (4km) section of new OHL. Install 3 x 700mm² (Araucaria) or 2 x 850mm² (Redwood) conductors on the new build section of the OHL, operating at 90°C. | EDF Energy Nuclear Generation Ltd | Hinkley 400kV Substation | Hinkley Point C | 01/06/2022
NGET-RI-20897L2 | Build a new circuit between the Hinkley Point leg of the broken Hinkley Point - Melksham OHL route and Seabank 400kV substation (~47km). Install 3 x 700mm² (Araucaria) or 2 x 850mm² (Redwood) conductors operating at 90°C. | EDF Energy Nuclear Generation Ltd | Hinkley 400kV Substation | Hinkley Point C | 01/06/2022
NGET-RI-20897L4 | Uprating the 275kV Hinkley Point - Bridgwater VQ route to 400kV operation and reconductoring from the tee point to Hinkley Point with GAP equivalent conductor. | EDF Energy Nuclear Generation Ltd | Hinkley 400kV Substation | Hinkley Point C | 01/06/2022
NGET-RI-20897Q | The work associated with the removal of the existing fluid fill cables at Hinkley Point site between the terminal tower of the VQ route and the Hinkley Point A substation (275kV). | EDF Energy Nuclear Generation Ltd | Hinkley 400kV Substation | Hinkley Point C | 01/06/2022
NGET-RI-20898 | Connecting new Hinkley Point - Seabank 1 circuit to the existing SGT4 bay. Tee-connect new Hinkley Point – Seabank 2 circuit to the existing Seabank – Melksham circuit at very close proximity to Seabank 400kV substation | EDF Energy Nuclear Generation Ltd | Hinkley 400kV Substation | Hinkley Point C | 01/06/2022
NGET-RI-20899 & 20899C | Replacing the 275kV disconnectors, earth switches, post insulators, CVTs and busbars at Bridgwater with 400kV equipment. Replacing the two 275/132kV SGTs at Bridgwater with two 400/275kV SGTs including associated protection. | EDF Energy Nuclear Generation Ltd | Hinkley 400kV Substation | Hinkley Point C | 01/06/2022
NGET-RI-21071-1L | Loop into the new Kings Lynn B 400kV substation to form a Walpole. The new 2.7km double circuit 400kV OHL route to Kings Lynn B Power Station rated to match that of the Walpole - Norwich route following the re-conductoring, namely 3x 700mm2 AAAC conductor sagged to a 75°C operating profile. | EP UK Power Developments Limited | Kings Lynn B 400kV Substation | Kings Lynn B | 31/10/2021
|  | 3R Energy Solutions | Coalburn132/33kV | Douglas West | 31/10/2021
NGET-RI-21071-1S | New 5 bay Kings Lynn B 400kV GIS substation and associated new LVAC protection and control works. This includes Current System generator intertripping scheme and New System generator intertripping facility. The scheme will also include extension of the existing East Anglia operational intertripping scheme. | EP UK Power Developments Limited | Kings Lynn B 400kV Substation | Kings Lynn B | 31/10/2021
NGET-RI-21132L | Construction of a short section of new OHL between the line entries of above two circuits at Melksham 400kv substation (approx 800m). | EDF Energy Nuclear Generation Ltd | Hinkley 400kV Substation | Hinkley Point C | 01/06/2022
NGET-RI-21132S | Swaps the Hinkley Point – Melksham 2 circuit and the Bramley Melksham 2 circuit line entries at Melksham 400kV substation. | EDF Energy Nuclear Generation Ltd | Hinkley 400kV Substation | Hinkley Point C | 01/06/2022
NGET-RI-21339S | • To provide one generator bay. • To modify existing busbar protection to include the new generation connection. • To install ancillary services monitoring equipment. | Spalding Energy Expansion Limited | Spalding | Spalding Energy Expansion
NGET-RI-21343-13 | New bus coupler to be installed at Raleigh Main 400kV substation and re-distribution of the ZT circuits such that Bradwell - Rayleigh circuit 1 is re-distributed to the Rayleigh main busbar 1. Involves moving the Rayleigh Main - Coryton South circuit southwards to allow room to extend Rayleigh Main. This work will be conducted at the same time as that associated with works at Rayleigh associated with the connection of a new Rayleigh - Bradwell 400kV double circuit. | InterGen (UK) Ltd | Coryton South 400kV Substation | Gateway Energy Centre Power Station | 30/09/2021
NGET-RI-21343-15 | Replace in situ existing OIBR bus section bay X120, bus coupler X130 and SGT1 and 4 bays X110, X410 respectively. | InterGen (UK) Ltd | Coryton South 400kV Substation | Gateway Energy Centre Power Station | 30/09/2021
NGET-RI-21343-23 | Installation of necessary equipment to provide provision for a generator intertripping scheme at Coryton South 400kV to manage local outage/fault combinations on the circuits connecting the Coryton South - Tilbury - Grain or X205 (at Coryton South) & Rayleigh - Coryton South or X605 (at Rayleigh). | InterGen (UK) Ltd | Coryton South 400kV Substation | Gateway Energy Centre Power Station | 30/09/2021
NGET-RI-21406S | Extension of 400kV busbars and substation building and installation of series reactor for generation connections at Killingholme 400kV Substation. Extension to the existing South Humber Bank Operational Tripping Scheme | C.GEN Killingholme Ltd | C.Gen North Killingholme | C.Gen Killingholme North Power Station | 01/04/2021
NGET-RI-21535S, NGET-RI-21535C & NGET-RI-21535T1, 21535T2 | A new GSP at Sandford to supply WPD as a consequence of taking over WPD's 132kV 'F' route to construct the new Hinkley Point - Seabank OHL. | EDF Energy Nuclear Generation Ltd | Hinkley 400kV Substation | Hinkley Point C | 01/06/2022
NGET-RI-21588 | Re-conductor the Dungeness - Sellindge OHL circuits to increase capacity. | South Eastern Power Networks |  | Ninefield
|  | South Eastern Power Networks |  | Canterbury North
|  | Seagreen Wind Energy Ltd | Tealing 275/33kv | Firth of Forth Offshore Wind Farm 1A | 30/06/2019
|  | South Eastern Power Networks |  | Bolney
NGET-RI-21631-1 | Install 2 x 400/132kV SGTs at Washway farm and 4 x 400/275kV interbus transformers at Kirkby. | NuGeneration Ltd | Moorside 400kV Substation | Moorside
NGET-RI-21631-2 | Uprate the 275kV circuit from Penwortham to Kirkby via Washway Farm. | NuGeneration Ltd | Moorside 400kV Substation | Moorside
NGET-RI-21632-1 | Reconductor Penworth - Padiham 400kV circuit. | NuGeneration Ltd | Moorside 400kV Substation | Moorside
NGET-RI-21637-1 | Construct new 400/132kV demand connection substation at Roosecote and Stainburn complete with new 400/132kV SGTs and also a 400kV GIS substation at Middleton, connected via a double turn-in of the Heysham - Quernmore Tee circuits with a series reactor on each of the new Heysham - Middleton circuits. | NuGeneration Ltd | Moorside 400kV Substation | Moorside
NGET-RI-21637-2 | Construct a new 400kV double circuit overhead line Harker 400kV to Stainburn 400kV, Stainburn 400kV to Moorside 400kV, Moorside 400kV to Roosecote 400kV and the cable circuit in a new tunnel from Roosecote 400kV to Middleton 400kV. | NuGeneration Ltd | Moorside 400kV Substation | Moorside
NGET-RI-21644-1 | Increase the capacity of the existing Penwortham cables on the Heysham - Stanah - Penwortham circuits. | NuGeneration Ltd | Moorside 400kV Substation | Moorside
NGET-RI-21765-1 | Extend and convert the existing Bicker Fen 400kV substation to a double busbar AIS substation with 4 feeder bays, 2 transformer bays, 1 bus coupler bays and 2 skeleton bus section bays to accommodating the existing 4 circuits and 2 transformers. Build 4 feeder bays, 2 transformer bays and one bus coupler and fully equip these bays. Modify the existing protection scheme to include 4 feeders, 2 transformers and one bus coupler. | Triton Knoll Offshore Wind Farm Ltd | Triton Knoll Offshore Substation | Triton Knoll Offshore Wind Farm | 13/08/2019
|  | Spalding Energy Expansion Limited | Spalding | Spalding Energy Expansion
NGET-RI-21765S | Extend Bicker Fen 400kV AIS double busbar substation with two additional skeleton generator bays. | Triton Knoll Offshore Wind Farm Ltd | Triton Knoll Offshore Substation | Triton Knoll Offshore Wind Farm | 13/08/2019
NGET-RI-21850 | Up-Rating of Rayleigh - Coryton South - Tilbury double circuit. | InterGen (UK) Ltd | Coryton South 400kV Substation | Gateway Energy Centre Power Station | 30/09/2021
NGET-RI-30029S | Construct a new 15 bay Moorside 400kV GIS double substation to include 4 new feeder circuit bays, 4 busbar section bays, 2 busbar coupler bays, 3 skeletal GIS generator bays and 2 skeletal GIS SGT bays. | NuGeneration Ltd | Moorside 400kV Substation | Moorside
NGET-RI-30106 | Reconductor the Trawsfynydd legs of the Deeside - Trawsfynydd - Legacy circuits with GAP conductor. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Horizon Nuclear Power Wylfa Limited | Wylfa 400kV Substation | Wylfa Newydd
|  | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-30145L | Double tee the Norwich - Walpole double circuit into the new Necton 400kV substation to form the Norwich - Necton - Walpole 1 and 2 circuits. | 3R Energy Solutions | Coalburn132/33kV | Douglas West | 31/10/2021
NGET-RI-30145S | Construction of a five bay 400kV AIS substation at Necton including two feeder bays, one coupler bay and two skeleton OFTO bays. Installation of a system - generator intertrip. | 3R Energy Solutions | Coalburn132/33kV | Douglas West | 31/10/2021
NGET-RI-30145S1 | Install an additional circuit breaker at Norwich Main on the current Walpole - Norwich 1 circuit to remove the circuit complexity restriction and allow the tee in at the new Necton 400kV substation. | 3R Energy Solutions | Coalburn132/33kV | Douglas West | 31/10/2021
NGET-RI-30203 & SPT-RI-123 | These works are part of the West Coast HVDC project. | RES UK & Ireland Limited | Carradale | Blary Hill Wind Farm
NGET-RI-30204 & SHETL-RI-025B | Construct a 2GW East Coast HVDC Link between Aberdeenshire and North East England. | NorthConnect KS | Peterhead 400KV | Norway Interconnector | 31/12/2022
NGET-RI-30308 | Install series compensation at Trawsfynydd 400kV Substation | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Horizon Nuclear Power Wylfa Limited | Wylfa 400kV Substation | Wylfa Newydd
|  | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-30309 | Installation of series compensation in the Pentir - Trawsfynydd 1 and Pentir - Trawsfynydd 2 circuits. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Horizon Nuclear Power Wylfa Limited | Wylfa 400kV Substation | Wylfa Newydd
|  | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-30310 | Establish a new 400kV double circuit OHL route between the existing Wylfa substation and Pentir substation to create the Wylfa - Pentir 3 and Wylfa - Pentir 4 circuits. | Horizon Nuclear Power Wylfa Limited | Wylfa 400kV Substation | Wylfa Newydd
NGET-RI-30311 | Stage 1 - Establish a second 400kV circuit between Pentir and Trawsfyndd comprising following elements a) Establishing a new 400kV 3 bay single switch mesh AIS substation at Penisarwaun. This substation will connect the Pentir – Dinorwig 2 - Trawsfynydd 400kV circuits; b) Installation of approximately 6 km of 2 cores per phase XLPE cable to cross the Glaslyn Estuary. c) Reconductor the existing sections of OHL between Penisarwaun and Trawsfynydd with 2 x 700mm2. d) Connect the circuit into the existing disconnector bay on Mesh Corner 3 at Trawsfynydd 400kV substation. e) Installation of a F3 ferroresonance quenching scheme on the SGT 3 Disconnector. Stage 2 - Increase the thermal capability of the existing Pentir - Trawsfynydd 400kV circuit. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Horizon Nuclear Power Wylfa Limited | Wylfa 400kV Substation | Wylfa Newydd
|  | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-30311-1L | Increase the thermal capability of the existing Pentir - Trawsfynydd 400kV circuit. | Horizon Nuclear Power Wylfa Limited | Wylfa 400kV Substation | Wylfa Newydd
NGET-RI-30311-1S | Increase the thermal capability of the existing Pentir - Trawsfynydd 400kV circuit. | Horizon Nuclear Power Wylfa Limited | Wylfa 400kV Substation | Wylfa Newydd
NGET-RI-30311-3C | Increase the thermal capability of the existing Pentir - Trawsfynydd 400kV circuit. | Horizon Nuclear Power Wylfa Limited | Wylfa 400kV Substation | Wylfa Newydd
NGET-RI-30345 | Reconfigure Wylfa 400kV substation by removing two SGTs and re-using the space to connect the new Wylfa-Pentir double circuit. | Horizon Nuclear Power Wylfa Limited | Wylfa 400kV Substation | Wylfa Newydd
NGET-RI-30346S | Installation of a 2750MVA 2% impendence series reactor at Pentir 400kV substation | Horizon Nuclear Power Wylfa Limited | Wylfa 400kV Substation | Wylfa Newydd
NGET-RI-30544 | Extension of 400kV busbars and installation of bus section breakers and bus coupler for generation connections at the Western side of Killingholme 400kV Substation. | Vi Aura Limited | Hornsea Platform 1C Offshore Substation | Hornsea Power Station 1C | 01/07/2020
|  | Heron Wind Ltd | Hornsea Platform 1A Offshore Substation | Hornsea Power Station 1A | 30/09/2019
|  | Njord Ltd | Hornsea Platform 1B Offshore Substation | Hornsea Power Station 1B | 28/02/2020
|  | C.GEN Killingholme Ltd | C.Gen North Killingholme | C.Gen Killingholme North Power Station | 01/04/2021
NGET-RI-30669-1 & SHETL-RI-033 | Install a second 2GW HVDC converter station with associated equipment. HVDC cables to be routed between Aberdeenshire and North East England. | NorthConnect KS | Peterhead 400KV | Norway Interconnector | 31/12/2022
NGET-RI-30752 | Creation of a new South West Operational Tripping Scheme (OTS) at Taunton. | Scottish & Southern Electricity Power Distribution |  | Lovedean
|  | Scottish & Southern Electricity Power Distribution |  | Mannington
|  | Scottish & Southern Electricity Power Distribution |  | Fawley
|  | Scottish & Southern Electricity Power Distribution |  | Axminster
|  | Scottish & Southern Electricity Power Distribution |  | Nursling
|  | Western Power Distribution (South West) Plc |  | Abham
|  | Scottish & Southern Electricity Power Distribution |  | Chickerell
|  | Scottish & Southern Electricity Power Distribution |  | Botley Wood
NGET-RI-30915 | Design, construct and commission a 2.5GW capacity VSC HVDC link from Wylfa to Pembroke comprising of a 2.5GW VSC based HVDC converter station local to the company's owned Wylfa 400kV substation in North Wales, a 2.5GW VSC based HVDC converter station local to the company's owned Pembroke 400kV substation in South Wales and a 2.5GW capacity HVDC linking the converter stations at Wylfa and Pembroke. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Organic Power Ltd | Connahs Quay 400kV | Marex
NGET-RI-30967 & NGET-RI-30968 | Construction of a new Sellindge double busbar bypass 400kV Substation. | South Eastern Power Networks |  | Ninefield
|  | South Eastern Power Networks |  | Canterbury North
|  | Seagreen Wind Energy Ltd | Tealing 275/33kv | Firth of Forth Offshore Wind Farm 1A | 30/06/2019
|  | South Eastern Power Networks |  | Bolney
NGET-RI-31154L1 | New Blyth 400kV substation OHL turn-in works. | National Grid NS Link Ltd | Blyth | NS Link | 30/09/2020
NGET-RI-31154L2 | Hotwire 275kV circuits in the North East. | National Grid NS Link Ltd | Blyth | NS Link | 30/09/2020
NGET-RI-31154S1 | Build a new 400kV substation at Blyth. | National Grid NS Link Ltd | Blyth | NS Link | 30/09/2020
NGET-RI-31338, NGET-RI-31339 & NGET-RI-21497-5 | Installation of Flexible AC Transmission Solutions (FACTS) at Bolney, Ninfield and Richborough and associated works. | South Eastern Power Networks |  | Ninefield
|  | South Eastern Power Networks |  | Canterbury North
|  | Seagreen Wind Energy Ltd | Tealing 275/33kv | Firth of Forth Offshore Wind Farm 1A | 30/06/2019
|  | South Eastern Power Networks |  | Bolney
NGET-RI-31569 | Extend Creyke Beck 400kV Substation to make available a single skeletal generator bay for the Relevant Transmission Licensee at the Interface, assuming a single offshore transmission circuit. | Forewind Ltd | Dogger Bank 220/33kV Offshore Substations | Dogger Bank Platform 1 | 01/04/2021
NGET-RI-31671 | Turn in 400kV Fawley - Botley Wood/Lovedean circuits into it. Installing a shunt reactor on this site and connecting the User's 400kV AC cable from the User's converter station in this substation. | National Grid International Ltd | Chilling 400KV Substation | IFA2 Interconnector | 31/10/2019
NGET-RI-31671-1 | Re-conductor the Bramley - Fleet OHL circuits to increase capacity. | Scottish & Southern Electricity Power Distribution |  | Lovedean
|  | Scottish & Southern Electricity Power Distribution |  | Mannington
|  | Scottish & Southern Electricity Power Distribution |  | Fawley
|  | Scottish & Southern Electricity Power Distribution |  | Axminster
|  | Scottish & Southern Electricity Power Distribution |  | Nursling
|  | Western Power Distribution (South West) Plc |  | Abham
|  | Scottish & Southern Electricity Power Distribution |  | Chickerell
|  | Scottish & Southern Electricity Power Distribution |  | Botley Wood
NGET-RI-31671-2 | Re-conductor the Fleet - Lovedean OHL circuits to increase capacity. | Scottish & Southern Electricity Power Distribution |  | Lovedean
|  | Scottish & Southern Electricity Power Distribution |  | Mannington
|  | Scottish & Southern Electricity Power Distribution |  | Fawley
|  | Scottish & Southern Electricity Power Distribution |  | Axminster
|  | Scottish & Southern Electricity Power Distribution |  | Nursling
|  | Western Power Distribution (South West) Plc |  | Abham
|  | Scottish & Southern Electricity Power Distribution |  | Chickerell
|  | Scottish & Southern Electricity Power Distribution |  | Botley Wood
NGET-RI-31813I | Extension of Pembroke 400kV substation building on both sides to accommodate two new GIS bays. Planning and consenting, if required, for the building extension. Double up of circuit breakers in 3 bus sections (X120, X220 and X320) and 2 bus coupler (X130 and X430) circuit breaker bays to satisfy loss of generation infeed requirement of the NETS SQSS. Extensions to Main bar 4 and Reserve bar 3/4 and main bar 1 and reserve bar 1/2 to extend the Pembroke 400kV busbar; provision and installation of two 400kV bay to facilitate the connection of Greenwire generation circuits. Replacement of all feeder circuit breakers and modification of feeder protections. Busbar protection replacement and substation control system modifications as required at Pembroke 400kV substation. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Greenwire Transmission Pembroke Limited | Pembroke 400kV Substation | Greenlink
NGET-RI-31829 | Establish a new 400kV GIS substation at Pentir 400kV | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
NGET-RI-31829 | Extend Pentir 400kV and establish one unpopulated skeletal AIS generator bay, including mitigation of SP Manweb owned 132kV circuits which traverse part of the extended substation site. Replace bus coupler circuit breaker X230 with two back-to-back circuit breakers. | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-31832S | The provision of one bus section bay and one bus coupler bay to facilitate the User connection at a new 400kV GIS 7 bay Sellindge substation. | ElecLink Ltd | Sellindge 400KV Substation | ElecLink
NGET-RI-31843L | Turn in of the Pembroke - Clifynydd and Pembroke - Walham 400kV circuits to Swansea North. | Greenwire Transmission Pembroke Limited | Pembroke 400kV Substation | Greenlink
NGET-RI-31843S | Extend the existing GIS 400kV double busbar at Swansea North by installing of a new bus coupler bay, a circuit breaker in reserve bus section and addition of new bay to connect SGT4A. | Greenwire Transmission Pembroke Limited | Pembroke 400kV Substation | Greenlink
NGET-RI-31990L | Reconductor Taunton - Alverdiscott circuit with Triple Araucaria. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
NGET-RI-32014S1 | Install two new MSCDN's at Ironbridge 400kV substation. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Organic Power Ltd | Connahs Quay 400kV | Marex
|  | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-32014S2 | Install two MSCDN's at Connah's Quay. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Organic Power Ltd | Connahs Quay 400kV | Marex
|  | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-32014S3 | Install two MSCDN's at Legacy 400kV. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Organic Power Ltd | Connahs Quay 400kV | Marex
|  | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-32018 | Re-conductor the overhead line from Pentir - Deeside 400kV substation with Triple Araucaria. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-32021 | Reconductor the Cellarhead - Drakelow 400kV circuit with 2 x 620mm² GZTACSR. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Organic Power Ltd | Connahs Quay 400kV | Marex
|  | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-32022 | Increase the thermal capability of the existing South Manchester - Bredbury 275kV circuit. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Organic Power Ltd | Connahs Quay 400kV | Marex
|  | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-32028 | Reconductor the Legacy - Shrewsbury - Ironbridge circuits with GAP conductor. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Organic Power Ltd | Connahs Quay 400kV | Marex
NGET-RI-32029 | Reconductor the Legacy legs of the Deeside - Trawsfynydd - Legacy circuits with GAP conductor. Reconductor the Legacy - Shrewsbury - Ironbridge circuits with GAP conductor. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Organic Power Ltd | Connahs Quay 400kV | Marex
|  | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-32030 | Uprate the two Quad Boosters at Legacy to 2750MVA. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Organic Power Ltd | Connahs Quay 400kV | Marex
|  | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-32056 | Establish one unpopulated skeletal generator bay in the Pentir 400kV GIS substation. | Codling Wind Park Ltd | Pentir Substation | Codling Park Wind Farm
|  | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-32105 | Reconductor Harker – Gretna – Hawick circuit. Uprate the V route 132kV overload line circuit (between Tower V075 and Harker 132kV substation) to provide a minimum summer pre-fault continuous rating of 170MVA. (NGET-RI-32105) | Loganhead Wind Farm Limited | EWE HILL WF 33/132KV COLLECTOR SUBSTATION | Loganhead Windfarm | 31/10/2023
NGET-RI-32144 | Provision of a new system-generator operational intertripping system for East Anglia and associated extension to include Galloper Offshore Wind Farm. | Galloper Wind Farm Limited | Galloper North 132/33kv | Galloper Wind Farm | 01/01/2017
NGET-RI-32278SI | Extend the busbar and a GIS skeletal bay and the associated foundation to provide 490MW CCGT connection. | C.GEN Killingholme Ltd | C.Gen North Killingholme | C.Gen Killingholme North Power Station | 01/04/2021
NGET-RI-32281 | Establish one unpopulated skeletal generator bay in the Pentir 400kV GIS substation. | Organic Power Ltd | Connahs Quay 400kV | Marex
NGET-RI-32372LI | Increase thermal rating of Carrington - South Manchester circuit. | Organic Power Ltd | Connahs Quay 400kV | Marex
NGET-RI-32373LI | Reconductor Connah's Quay - Daines circuit with London. | Organic Power Ltd | Connahs Quay 400kV | Marex
NGET-RI-32374LI | Increase thermal rating of Cellarhead - Daines cable. | Organic Power Ltd | Connahs Quay 400kV | Marex
NGET-RI-32473LI & NGET-RI-32473CI | Installation of new terminal towers on the Norwich - Bramford circuits and removal of the existing suspension towers. Installation of the cable circuit to duck tee connection underneath OHL. | Progress Power Ltd | Yaxley 400kV Substation | Progress Power Station | 30/09/2019
NGET-RI-32473SI | Installation of a new double busbar 400kV substation with associated feeder bays, coupler bay and skeleton generator bay and provide double tee connection of the new substation to the Norwich - Bramford double OHL circuit. | Progress Power Ltd | Yaxley 400kV Substation | Progress Power Station | 30/09/2019
NGET-RI-32589 | Minor substation amendments at Wylfa 400kV. | Horizon Nuclear Power Wylfa Limited | Wylfa 400kV Substation | Wylfa Newydd
NGET-RI-32640SI | Uprate circuit breakers at Penwortham 400kV substation, Daines 400kV substation, Harker 275kV substation, Kearsley 275kV substation, Fiddlers Ferry 275kV substation and Carrington 400kV substation. | NuGeneration Ltd | Moorside 400kV Substation | Moorside
NGET-RI-32646LI | Reconductor Hambleton Tee - Penwortham 400kV circuits as well as Carrington - Penwortham 400kV circuit. | NuGeneration Ltd | Moorside 400kV Substation | Moorside
NGET-RI-32655 | Installation of Operational tripping scheme. | Horizon Nuclear Power Wylfa Limited | Wylfa 400kV Substation | Wylfa Newydd
NGET-RI-32928 | Reconductor the Legacy - Shrewsbury - Ironbridge circuits with GAP conductor. | Greenwire Transmission Pentir Limited | Pentir 400kV Substation | Greenwire Wind Farm - Pentir
NGET-RI-33539 | Hot wiring of the Hinckley Point - Melksham 1 and 2 circuits to increase their thermal rating. | Scottish & Southern Electricity Power Distribution |  | Mannington
|  | Scottish & Southern Electricity Power Distribution |  | Axminster
|  | Western Power Distribution (South West) Plc |  | Abham
|  | Scottish & Southern Electricity Power Distribution |  | Chickerell
NGET-TI-30145LC | OHL modification to accommodate new circuit breaker at Norwich main. | 3R Energy Solutions | Coalburn132/33kV | Douglas West | 31/10/2021
NLEI Item 1 | Installation of a 275kV and 132kV switchbay at Elvanfoot substation, connecting to a 240MVA 275/132kV transformer (SGT2D). | NLEI Limited |  | North Lowther Energy Initiative | 31/10/2022
NLEI Item 2 | Installation of approximately 14km overhead line between Elvanfoot 132kV substation and NLEI wind farm. | NLEI Limited |  | North Lowther Energy Initiative | 31/10/2022
NLEI Item 3 | Installation of two 132kV line isolators at NLEI Wind Farm. | NLEI Limited |  | North Lowther Energy Initiative | 31/10/2022
None identified at this time |  | Crookedstane Windfarm Limited | Crookedstane Windfarm Substation | Crookedstane Windfarm | 30/10/2017
|  | Pogbie Wind Farm Limited | Pogbie 33kV Substation | Pogbie Wind Farm
|  | RES UK & Ireland Limited | Chapelcross 132/33Kv Substation | Solwaybank
|  | Islay Tidal Power Limited | Port Ann GSP | Sound of Islay Tidal | 30/11/2017
|  | Gilston Hill Windfarm Limited |  | Gilston Hill Wind Farm | 30/07/2023
|  | Whitelaw Brae Windfarm Limited | Whitelaw Brae 'A' and 'B' 33kV Substations | Whitelaw Brae Windfarm | 31/10/2019
Sandy Knowe Item 2 | Installation of 132kV overhead line (approximately 6.5km), and an optical fibre, between Glenglass 132/33kV substation and Sandy Knowe wind farm substation. | Sandy Knowe Wind Farm Ltd | Glenglass 132/33kv | Sandy Knowe Wind Farm | 30/10/2021
Sandy Knowe Item 3 | From the Sandy Knowe wind farm 132kV circuit installation of one line isolator. | Sandy Knowe Wind Farm Ltd | Glenglass 132/33kv | Sandy Knowe Wind Farm | 30/10/2021
Sanquhar IIa Item 1 | At Sanquhar II Wind Farm 132kV substation installation of one line isolator. | Sanquhar II Community Wind Company Limited |  | Sanquhar IIa Community Wind Farm | 30/11/2023
Sanquhar IIa Item 2 | Installation of 132kV wood pole overhead line (approximately 8km), and an optical fibre, between Sanquhar II wind farm 132kV substation and Glenmuckloch pump storage 132kV substation. | Sanquhar II Community Wind Company Limited |  | Sanquhar IIa Community Wind Farm | 30/11/2023
Sanquhar IIa Item 3 | At Glenmuckloch pump storage 132kV substation, a new (Relevant Transmission Licensee owned) 132kV circuit breaker and 132kV isolators and associated apparatus, will be installed. | Sanquhar II Community Wind Company Limited |  | Sanquhar IIa Community Wind Farm | 30/11/2023
Sanquhar IIa Item 4 | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of the Bilateral Connection Agreement. | Sanquhar II Community Wind Company Limited |  | Sanquhar IIa Community Wind Farm | 30/11/2023
Scoop Hill Item 1 | At Moffat 132kV substation install two 132kV feeder circuit breakers and associated switch bays. | Community Wind Power Ltd | Scoop Hill Wind Farm 132kV Substation | Scoop Hill Wind Farm | 31/12/2023
Scoop Hill Item 2 | Establish 2x 132kV circuit, incorporating 10km of underground cable and associated auxiliary cable, between Moffat 132kV Substation and Scoop Hill Wind Farm Substation | Community Wind Power Ltd | Scoop Hill Wind Farm 132kV Substation | Scoop Hill Wind Farm | 31/12/2023
Scoop Hill Item 3 | Provision of communications, alarms, indications and metering from the User site as set out in Appendix F of this Bilateral Connection Agreement. | Community Wind Power Ltd | Scoop Hill Wind Farm 132kV Substation | Scoop Hill Wind Farm | 31/12/2023
SHETL-RI-002 & SPT-RI-001A | Replace existing Beauly - Fort Augustus - Fasnakyle - Errochty - Braco - Bonnybridge 132kV double circuit line with 400kV construction, one circuit to be operated at 400kV and the other circuit at 275kV. Modify the existing substation arrangements at Beauly, Fasnakyle, Fort Augustus, Errochty and Braco to interface with the new line operating voltages. Construct a new Denny North 400/275/132kV substation. | Simec Lochaber Hydropower 2 Limited | Kinlochleven | Kinlochleven | 01/04/2022
|  | Achlachan Wind Farm LLP |  | Achlachan
|  | Tullymurdoch Limited | Coupar Angus | Tullymurdoch Wind Farm | 30/11/2016
|  | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
|  | PNE Wind UK Ltd | Elgin 275/132kV Substation | Meikle Hill Wind Farm | 31/10/2020
|  | Innogy Renewables UK Ltd | Mybster 132/33kV | Bad a Cheo Wind Farm
|  | Wathegar 2 Limited | Mybster 1 | Wathegar 2 Windfarm | 31/12/2018
|  | Falck Renewables Wind Ltd | Millennium South 132/33kV Substation | Millennium South | 30/09/2016
|  | Simec Lochaber Hydropower 2 Limited | Fort William 33kV substation | Lochaber | 31/10/2018
|  | Brims Tidal Array Limited | Bay of Skaill 132/33kV substation | Cantick Head
|  | Vattenfall Wind Power Ltd | Cairnford | Clashindarroch 2
|  | Lark Energy Limited | Arbroath GSP | Greenford Farm Solar Farm | 31/03/2016
|  | Hywind (Scotland) Ltd | Peterhead Grange | Hywind Wind Farm | 31/03/2017
|  | SSE Generation Ltd | Stronelairg 132/33kV Substation | Stronelairg | 31/03/2017
|  | Kincardine Offshore Wind Limited | Redmoss 132/33kV Grid Supply Point Substation | Kincardine Offshore Wind Farm | 30/06/2018
|  | Elchies Wind Limited | Elchies 132/33kV Substation | Elchies Wind Farm
|  | Kilmac Energy | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm
SHETL-RI-004 | Reconductor the Beauly - Foyers - Blackhillock 275kV double circuit line with larger capacity conductor between Beauly - Knocknagael and between Knocknagael - Blackhillock and Blackhillock - Kintore (XH1/XH2). The substation at Knocknagael is adjacent to the existing Foyers line tee point. | PNE Wind UK Ltd | Elgin 275/132kV Substation | Meikle Hill Wind Farm | 31/10/2020
|  | Speyside Renewable Energy Partnership Ltd | Keith 132/33kV | Speyside CHP
|  | Vattenfall Wind Power Ltd | Cairnford | Clashindarroch 2
SHETL-RI-005 | Extend both the 275kV and 132kV busbars and install a second 275/132kV interbus auto-transformer at Dounreay substation. Upgrade the existing 150MVA interbus auto-transformer at Dounreay to 240MVA. | Brims Tidal Array Limited | Bay of Skaill 132/33kV substation | Cantick Head
SHETL-RI-006 | Install two x 240MVA 220kV 3.6km underground cable circuits from a transition joint near Ardneil bay to Hunterston. Develop a new transformer compound at Hunterston comprising 2 x 400/220kV 240MVA transformers, each equipped with tertiary connected 60MVAr shunt reactors. Install two new feeder bays of 400kV GIS double busbar switchgear at Hunterston East 400kV Substation and establish 400kV connections to the new transformer compound. Complete Associated civil works and other miscellaneous works including installation/modification of associated protection, control, telecommunications and metering equipment. | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
|  | Brims Tidal Array Limited | Bay of Skaill 132/33kV substation | Cantick Head
SHETL-RI-007B | Beauly 400kV Busbar — Construct a new 400kV GIS double busbar at Beauly substation and interface to the existing 275kV busbar. The 400kV double busbar to comprise a section breaker and a bus coupler. In addition, allowance should be made for 8 feeder bays. | Pentland Road Windfarm Ltd | Stornoway | Pentland Road
|  | EDF Energy Renewables Limited | Muaitheabhal 132/33kV Substation | Muaitheabhal Wind Farm
|  | Lewis Wind Power Ltd | Stornoway 132/33kV Substation | Stornoway Wind Farm
|  | Druim Leathann Windfarm Ltd | Druim Leathann 132/33kV substation | Druim Leathann | 31/12/2020
SHETL-RI-007C | Redevelop Blackhillock substation to enable the construction of new 400kV, 275kV and 132kV double busbars. | Westray South Tidal Development Limited | Crook 132/33kV Substation | Westray South
|  | Paul's Hill II Limited | Glenfarclas 132/33kV Substation | Paul's Hill II Wind Farm | 31/10/2021
|  | ScottishPower Renewables (UK) Limited | Mybster 132/33kV Substation | Halsary Wind Farm
|  | Beatrice Offshore Windfarm Ltd | Beatrice 33/132kV Offshore Substations | Beatrice Wind Farm | 01/04/2018
|  | Achlachan Wind Farm LLP |  | Achlachan
|  | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
|  | PNE Wind UK Ltd | Elgin 275/132kV Substation | Meikle Hill Wind Farm | 31/10/2020
|  | Innogy Renewables UK Ltd | Mybster 132/33kV | Bad a Cheo Wind Farm
|  | MeyGen Ltd | Gills Bay | MeyGen Tidal
|  | Wathegar 2 Limited | Mybster 1 | Wathegar 2 Windfarm | 31/12/2018
|  | Brims Tidal Array Limited | Bay of Skaill 132/33kV substation | Cantick Head
|  | Vattenfall Wind Power Ltd | Cairnford | Clashindarroch 2
|  | WKN Sallachy Ltd | Sallachy 132kV Substation | Sallachy Wind Farm
|  | RockbySea Ltd | Alness GSP | Coire Na Cloiche | 31/10/2018
|  | SSE Generation Ltd | Strathy North and Strathy South 132/33kV Substation | Strathy North and South Wind | 12/06/2015
|  | Dorenell Windfarm Limited | Dorenell 132/33kV | Dorenell Wind Farm | 01/04/2018
|  | Peel (Yell) Wind Farms Limited | Yell | Beaw Field Wind Farm
|  | Elchies Wind Limited | Elchies 132/33kV Substation | Elchies Wind Farm
|  | SSE Renewables Developments (UK) Ltd | Shin 33kV | Glencassley Wind Farm | 31/10/2022
|  | Aberarder Wind Farm LLP | Aberarder 132/33Kv Substation | Aberarder Wind Farm | 30/06/2020
|  | Rothes III Limited | Dallas 275/33kV Substation | Rothes III Wind Farm | 31/05/2021
|  | SCT Renewables Limited | Kergord | Viking Wind Farm
|  | Green Cat Renewable Developments Ltd | Brora GSP | Navidale Wind Farm | 31/10/2021
|  | Nanclach Limited | Boat of Garton | Tom Nan Clach | 31/03/2019
|  | SSE Generation Ltd | Gordonbush | Gordonbush Wind | 31/10/2022
|  | Creag Riabhach Wind Farm Ltd | Creag Riabhach 132/33kV Substation | Creag Riabhach Wind Farm
SHETL-RI-007c | Blackhillock Substation Redevelopment — Redevelop Blackhillock Substation to enable the construction of new 400kV, 275kV and 132kV double busbars. Connectivity is maintained by two 1200MVA 400/275kV SGTs and two 360MVA 275/132kV SGTs. Connect the existing three 240MVA 275/132kV SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. | Elgin Energy EsCo Limited | Elgin | Milltown Airfield Solar Farm | 31/10/2020
|  | Elgin Energy EsCo Limited | Elgin | Speyslaw Solar | 31/10/2020
|  | E.ON Climate & Renewables UK Developments Limited | Strathy Wood | Strathy Wood | 31/10/2021
SHETL-RI-009 & SPT-RI-004 | Upgrade the Blackhillock/Kintore/Kincardine 400kV East coast route by upgrading the existing 275kV circuits to 400kV operation. Establish New 400kV busbars at Rothienorman, Kintore and Alyth to enable this upgrade. SPT own Kincardine substation and will be responsible for all 400kV conversion works at this location. | Vattenfall Wind Power Ltd | Cairnford | Clashindarroch 2
SHETL-RI-011 | Establish a new 132kV switching station at Crossaig in Kintyre, complete with busbar connected reactive compensation (SVC). Connect in the existing 132kV double circuit line to Port Ann. Rebuild and connect in the existing 132kV double circuit line to Carradale. Establish two 132kV AC subsea cable circuits between the new switching station at Crossaig and the existing 132kV busbar at Hunterston. Establish a second 132/33kV transformer substation at Carradale. Establish a third 400/132kV 360MVA inter-bus transformer at Hunterston. | DP Marine Energy Limited | Carradale 132/33kV | West Islay Tidal | 30/04/2019
|  | Good Energy Development (No.7) Limited | Willow Wind 132/33kV | Willow Wind Farm | 01/04/2023
SHETL-RI-011 & SPT-RI-006 | Establish a new 132kV substation at Crossaig in Kintyre with reactive compensation equipment. Connect in the existing 132kV double circuit line to Port Ann with Quadrature Booster transformers in circuit at Crossaig. Rebuild and connect in the existing 132kV double circuit line to Carradale. Establish two 240MVA subsea cable circuits (or three 120MVA cable circuits) between the new substation at Crossaig and the existing 132kV busbar at Hunterston. | RES UK & Ireland Limited | Carradale | Blary Hill Wind Farm
|  | Fyne Futures Limited | Carradale 132/33kV Substation | Auchadaduie Wind Farm | 31/03/2017
SHETL-RI-013 | Establish a new 275/132kV Substation (Ardbrecknich) near the existing Inveraray/Taynuilt 132kV line route with two 360 MVA 275/132kV transformers. Space provision to be allowed for an additional two transformers in the future and additional feeder bays. Establish a 275kV double circuit OHL between Ardbrecknish and Dalmally Substations. | SSE Renewables Developments (UK) Ltd | Carradale | Tangy III Wind Farm | 01/04/2022
|  | ScottishPower Renewables (UK) Limited | Carradale 132/33kV Substation | Beinn an Tuirc 3
SHETL-RI-015a | Knocknagael – Tomatin 275/132kV Reinforcement - Reinforce the existing 132kV transmission network between Beauly–Farr–Boat of Garten (Circuits BR1/RG1/BR2/RG2). Note that the existing 132kV OHL passes close to Knocknagael substation. Establish a new 275/132kV substation station including a 132kV double busbar arrangement near Tomatin and connected to a new 275kV double circuit OHL from the Knocknagael 275kV busbar via 275/132kV SGTs. | Paul's Hill II Limited | Glenfarclas 132/33kV Substation | Paul's Hill II Wind Farm | 31/10/2021
|  | Innogy Renewables UK Ltd | Glen Kyllachy Wind Farm | Glen Kyllachy Wind Farm | 28/08/2019
|  | Nanclach Limited | Boat of Garton | Tom Nan Clach | 31/03/2019
SHETL-RI-015b | Beauly-Farr-Boat of Garten 132kV OHL Reconfiguration - The existing section of 132kV OHL (BR1 & BR2) between Beauly and Farr will be terminated on the 132kV busbar at Knocknagael Substation. The OHL sections of the existing 132kV OHL will be dismantled between Knocknagael and Farr as part of the 132kV OHL reconfiguration. The existing section of double circuit 132kV OHL (RG1 & RG2) between Farr and Boat of Garten will be reconfigured as radial circuits between Tomatin and Boat of Garten. A normally open (N/O) point will be required at Keith on the circuit (FK) between Glenfarclas and Keith. This arrangement will leave Glenfarclas on a radial circuit fed from Boat of Garten under normal operating conditions. | Paul's Hill II Limited | Glenfarclas 132/33kV Substation | Paul's Hill II Wind Farm | 31/10/2021
|  | Nanclach Limited | Boat of Garton | Tom Nan Clach | 31/03/2019
SHETL-RI-019 | Establishment of a single 132kV AC circuit over a distance of approximately 70km between the proposed new 275kV GIS substation at Dounreay on the mainland and the new 132kV substation at the Bay of Skaill on Orkney. The 132kV circuit will comprise 9km of land cable and 91km of subsea cable element. Reactive compensation devices will be installed at both cable ends within the substation compounds at Dounreay and the Bay of Skaill. Two 33kV busbars complete with reactors will be installed and each connected to the 132kV busbars via two 120MVA 132/33kV GT's (four in total). | Westray South Tidal Development Limited | Crook 132/33kV Substation | Westray South
|  | Brims Tidal Array Limited | Bay of Skaill 132/33kV substation | Cantick Head
SHETL-RI-020 | Establish an HVDC link from Orkney to Peterhead in a phased manner to allow connection of marine and other renewable generation on and around the coast of Orkney. The works included in comprise an extension to the 132kV double busbar substation and a 600MW HVDC link from the northwest coast of Orkney to a HVDC switching station located inland in the vicinity of Sinclair’s Bay in Caithness. The HVDC link between Northwest Orkney and Sinclair’s Bay will have both land and subsea cable sections. | Westray South Tidal Development Limited | Crook 132/33kV Substation | Westray South
|  | Brims Tidal Array Limited | Bay of Skaill 132/33kV substation | Cantick Head
SHETL-RI-021 | Establish an HVDC link from Orkney to Peterhead in a phased manner to allow connection of marine and other renewable generation on and around the coast of Orkney. The works included in includes the 1200MW HVDC link to Peterhead and the HVDC switching station. The HVDC link between Northwest Orkney and Sinclair’s Bay will have both land and subsea cable sections. | Westray South Tidal Development Limited | Crook 132/33kV Substation | Westray South
|  | Brims Tidal Array Limited | Bay of Skaill 132/33kV substation | Cantick Head
SHETL-RI-025C | Construct a new 400kV substation close to the existing 275kV substation at Peterhead. Install two new 1000MVA 400/275kV Supergrid Transformers (SGT5 & SGT6) between the new 400kV busbars and the existing 275kV busbars. Modify the existing 275/132kV supergrid transformer SGT1 which is currently connected to line circuit reference VX1 will be banked with SGT5 1000MVA 400/275kV. | Westray South Tidal Development Limited | Crook 132/33kV Substation | Westray South
SHETL-RI-031 | As part of the Caithness - Moray Firth transmission reinforcement it is required to construct a HVDC link from Spittal to Blackhillock via a HVDC joint box at Noss Head and a new 275/132kV busbar arrangement at Spittal (5km North of Mybster). | Westray South Tidal Development Limited | Crook 132/33kV Substation | Westray South
|  | ScottishPower Renewables (UK) Limited | Mybster 132/33kV Substation | Halsary Wind Farm
|  | E.ON Climate & Renewables UK Developments Limited | Golticlay 132/33kV | Golticlay Wind Farm | 31/10/2022
|  | Achlachan Wind Farm LLP |  | Achlachan
|  | Innogy Renewables UK Ltd | Mybster 132/33kV | Bad a Cheo Wind Farm
|  | MeyGen Ltd | Gills Bay | MeyGen Tidal
|  | Wathegar 2 Limited | Mybster 1 | Wathegar 2 Windfarm | 31/12/2018
|  | Brims Tidal Array Limited | Bay of Skaill 132/33kV substation | Cantick Head
|  | WKN Sallachy Ltd | Sallachy 132kV Substation | Sallachy Wind Farm
|  | RockbySea Ltd | Alness GSP | Coire Na Cloiche | 31/10/2018
|  | SSE Generation Ltd | Strathy North and Strathy South 132/33kV Substation | Strathy North and South Wind | 12/06/2015
|  | E.ON Climate & Renewables UK Developments Limited | Strathy Wood | Strathy Wood | 31/10/2021
|  | Peel (Yell) Wind Farms Limited | Yell | Beaw Field Wind Farm
|  | SSE Renewables Developments (UK) Ltd | Shin 33kV | Glencassley Wind Farm | 31/10/2022
|  | SCT Renewables Limited | Kergord | Viking Wind Farm
|  | Green Cat Renewable Developments Ltd | Brora GSP | Navidale Wind Farm | 31/10/2021
|  | SSE Generation Ltd | Gordonbush | Gordonbush Wind | 31/10/2022
|  | Creag Riabhach Wind Farm Ltd | Creag Riabhach 132/33kV Substation | Creag Riabhach Wind Farm
SHETL-RI-032A | A new 275kV overhead line and substation works between Dounreay, Thurso and Spittal Substations. | Achlachan Wind Farm LLP |  | Achlachan
|  | Innogy Renewables UK Ltd | Mybster 132/33kV | Bad a Cheo Wind Farm
|  | MeyGen Ltd | Gills Bay | MeyGen Tidal
|  | Wathegar 2 Limited | Mybster 1 | Wathegar 2 Windfarm | 31/12/2018
|  | Brims Tidal Array Limited | Bay of Skaill 132/33kV substation | Cantick Head
|  | WKN Sallachy Ltd | Sallachy 132kV Substation | Sallachy Wind Farm
|  | SSE Generation Ltd | Strathy North and Strathy South 132/33kV Substation | Strathy North and South Wind | 12/06/2015
|  | E.ON Climate & Renewables UK Developments Limited | Strathy Wood | Strathy Wood | 31/10/2021
|  | SSE Renewables Developments (UK) Ltd | Shin 33kV | Glencassley Wind Farm | 31/10/2022
|  | SSE Generation Ltd | Gordonbush | Gordonbush Wind | 31/10/2022
|  | Creag Riabhach Wind Farm Ltd | Creag Riabhach 132/33kV Substation | Creag Riabhach Wind Farm
SHETL-RI-032B | Reinforce the existing 132kV double circuit overhead line between Dounreay, Thurso and Mybster substation (UTN/UTS and part of TME/TMW) Via a new 275/132kV substation at Spittal. | ScottishPower Renewables (UK) Limited | Mybster 132/33kV Substation | Halsary Wind Farm
|  | Achlachan Wind Farm LLP |  | Achlachan
|  | Innogy Renewables UK Ltd | Mybster 132/33kV | Bad a Cheo Wind Farm
|  | Wathegar 2 Limited | Mybster 1 | Wathegar 2 Windfarm | 31/12/2018
SHETL-RI-035 | Construct a new 275/132kV substation near Loch Buidhe, at the crossing point of the existing Beauly - Dounreay 275kV and Shin - Mybster 132kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kV Beauly - Dounreay and 132kV Shin - Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kV double busbar to the new 132kV double busbar via two 240MVA 275.132kV SGTs. | Achlachan Wind Farm LLP |  | Achlachan
|  | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
|  | Innogy Renewables UK Ltd | Mybster 132/33kV | Bad a Cheo Wind Farm
|  | MeyGen Ltd | Gills Bay | MeyGen Tidal
|  | Wathegar 2 Limited | Mybster 1 | Wathegar 2 Windfarm | 31/12/2018
|  | WKN Sallachy Ltd | Sallachy 132kV Substation | Sallachy Wind Farm
|  | RockbySea Ltd | Alness GSP | Coire Na Cloiche | 31/10/2018
|  | SSE Generation Ltd | Strathy North and Strathy South 132/33kV Substation | Strathy North and South Wind | 12/06/2015
|  | E.ON Climate & Renewables UK Developments Limited | Strathy Wood | Strathy Wood | 31/10/2021
|  | SSE Renewables Developments (UK) Ltd | Shin 33kV | Glencassley Wind Farm | 31/10/2022
|  | Green Cat Renewable Developments Ltd | Brora GSP | Navidale Wind Farm | 31/10/2021
|  | SSE Generation Ltd | Gordonbush | Gordonbush Wind | 31/10/2022
|  | Creag Riabhach Wind Farm Ltd | Creag Riabhach 132/33kV Substation | Creag Riabhach Wind Farm
SHETL-RI-036 | Reconductor part of the first 275kV circuits (BT1 - Beauly - Kilbraur - Gordonbush - Dounreay) between Beauly, new Fyrish and the new Loch Buidhe substation (FYL1/BFY1 circuit). The new conductor to be the same specification as the second 275kV circuit (BU2 circuit) between Beauly and Dounreay. | E.ON Climate & Renewables UK Developments Limited | Golticlay 132/33kV | Golticlay Wind Farm | 31/10/2022
|  | Achlachan Wind Farm LLP |  | Achlachan
|  | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
|  | Innogy Renewables UK Ltd | Mybster 132/33kV | Bad a Cheo Wind Farm
|  | MeyGen Ltd | Gills Bay | MeyGen Tidal
|  | Wathegar 2 Limited | Mybster 1 | Wathegar 2 Windfarm | 31/12/2018
|  | RockbySea Ltd | Alness GSP | Coire Na Cloiche | 31/10/2018
|  | SSE Generation Ltd | Strathy North and Strathy South 132/33kV Substation | Strathy North and South Wind | 12/06/2015
|  | E.ON Climate & Renewables UK Developments Limited | Strathy Wood | Strathy Wood | 31/10/2021
|  | SSE Renewables Developments (UK) Ltd | Shin 33kV | Glencassley Wind Farm | 31/10/2022
|  | SSE Generation Ltd | Gordonbush | Gordonbush Wind | 31/10/2022
|  | Creag Riabhach Wind Farm Ltd | Creag Riabhach 132/33kV Substation | Creag Riabhach Wind Farm
SHETL-RI-037 | Establish a new 275/132kV Fyrish substation close to the existing Alness 132kV OHL Tee location. The substation shall interface with the 275kV double-circuit between Beauly and Loch Buidhe. An optimal 132kV route will be designed and engineered to link the new 275/132kV Fyrish substation with the existing Alness GSP. | Achlachan Wind Farm LLP |  | Achlachan
|  | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
|  | Innogy Renewables UK Ltd | Mybster 132/33kV | Bad a Cheo Wind Farm
|  | Wathegar 2 Limited | Mybster 1 | Wathegar 2 Windfarm | 31/12/2018
|  | RockbySea Ltd | Alness GSP | Coire Na Cloiche | 31/10/2018
SHETL-RI-038 | Install an operational intertrip scheme on the Errochty - Tummel 132kV circuit breakers, at Errochty 132kV substation. | Innogy Renewables UK Ltd | Mybster 132/33kV | Bad a Cheo Wind Farm
SHETL-RI-042 | Western Isles HVDC Link — Establish a 600MW HVDC link with associated equipment and converter stations between the Western Isles (Arnish on Lewis) and the 400kV double busbar at Beauly (SHETL-RI-007b). The HVDC cable to be routed approximately 79km subsea cable, and approximately 80km by land cable. The HVDC infrastructure interface with a new 132kV double busbar at Arnish (Lewis) and the 400kV double busbar at Beauly. | Pentland Road Windfarm Ltd | Stornoway | Pentland Road
|  | EDF Energy Renewables Limited | Muaitheabhal 132/33kV Substation | Muaitheabhal Wind Farm
|  | Lewis Wind Power Ltd | Stornoway 132/33kV Substation | Stornoway Wind Farm
|  | Druim Leathann Windfarm Ltd | Druim Leathann 132/33kV substation | Druim Leathann | 31/12/2020
SHETL-RI-043 | Establish transmission infrastructure between a new 132kV double busbar a Gravir and a new 132kV double busbar arrangement at Stornoway GSP. The new 132kV infrastructure to be a mixture of cable and overhead lines routed approximately 22km by subsea and 6km by land. Interface the new 132kV infrastructure at Stornoway Grid with the 33kV network via 2 x 60MVA transformers and the existing 132kV overhead line from Harris. | Pentland Road Windfarm Ltd | Stornoway | Pentland Road
SHETL-RI-044 | Install a new 132kV OHL between Fort Augustus 132kV double busbar and SkyeTee. Connect the new 132kV OHL to a new 132kV circuit breakers at Fort Augustus. New 132kV Overhead line to be approximately 9km and to have a minimum rating equivalent to an ACSR lynx conductor at 50°C. Reinstate existing overhead line between Fort Augustus and Fort William. Modify any protection settings at Fort Augustus and Fort William for new arrangement. | Simec Lochaber Hydropower 2 Limited | Kinlochleven | Kinlochleven | 01/04/2022
|  | Falck Renewables Wind Ltd | Millennium South 132/33kV Substation | Millennium South | 30/09/2016
|  | Simec Lochaber Hydropower 2 Limited | Fort William 33kV substation | Lochaber | 31/10/2018
SHETL-RI-045 | Reconductor the 132kV double circuit OHL between Fort Augustus and Fort William (FFW/FFE). The 132kV double circuit OHL (FFE/FFE) is to be reconductored with a higher capacity conductor. This will have a minimum summer pre-fault rating of 130MVA per Circuit. Transfer the connection of Invergarry power station from FFE circuit of the OHL between Fort Augustus and Fort William to the FFW circuit. | Simec Lochaber Hydropower 2 Limited | Kinlochleven | Kinlochleven | 01/04/2022
SHETL-RI-047 | Bulk purchase of the series reactor at Killingholme 400kV Substation. | Speyside Renewable Energy Partnership Ltd | Keith 132/33kV | Speyside CHP
SHETL-RI-048 | Install a new fourth 240MVA 400/132kV SGT4 at Fort Augustus substation. Connect the new SGT to the existing 400kV OHL line Tee arrangement and 132kV double busbar. | Simec Lochaber Hydropower 2 Limited | Kinlochleven | Kinlochleven | 01/04/2022
SHETL-RI-050 | Reinforce the 132kV Transmission Network in the Kintyre Peninsula. Rebuild approximately 84km of 132kV double circuit OHL steel lattice construction between Inveraray, Port An and Crossaig. | SSE Renewables Developments (UK) Ltd | Carradale | Tangy III Wind Farm | 01/04/2022
|  | ScottishPower Renewables (UK) Limited | Carradale 132/33kV Substation | Beinn an Tuirc 3
SHETL-RI-052 | Establish a new 132kV double busbar arrangement at Lairg and build approximately 20km of new double circuit 132kV overhead tower line between Lairg and Loch Buidhe. It is expected that the first 10.5km of the new double circuit 132kV between Lairg and Loch Buidhe will be along the route of the existing Lairg - Shin (CS) 132kV OHL. A new route will have to be established for the remaining 9.5km (approx.) double circuit 132kV OHL. | WKN Sallachy Ltd | Sallachy 132kV Substation | Sallachy Wind Farm
|  | SSE Renewables Developments (UK) Ltd | Shin 33kV | Glencassley Wind Farm | 31/10/2022
|  | Creag Riabhach Wind Farm Ltd | Creag Riabhach 132/33kV Substation | Creag Riabhach Wind Farm
SHETL-RI-053 | It is required to construct a 600MW HVDC link from Shetland to the Scottish mainland at an HVDC switching station in the vicinity of Sinclair's Bay in Caithness. The HVDC switching station works will integrate with the Caithness-Moray Transmission Reinforcement. The HVDC link includes a 600MW HVDC converter station and 132kV substation at Kergord in Shetland. The new 132kV substation at Kergord will be the collection point for the large volume of wind generation in Shetland. The 600MW HVDC link will have approximately 13km of land cable and 284km of Subsea cable between Shetland and the HVDC switching station in Caithness. | Peel (Yell) Wind Farms Limited | Yell | Beaw Field Wind Farm
|  | SCT Renewables Limited | Kergord | Viking Wind Farm
SHETL-RI-055 | A compound will be established on the route of the existing 132kV Stornoway/Harris wood pole line at a suitable location to accommodate a new 132kV wood pole line from the newly established 132kV double busbar at Gravir. The new 132kV overhead line will be around 10km and have a minimum continuous rating of 150MVA. Two 132kV circuit breakers will be accommodated in the compound around the selected Tee point. A fully equipped 132kV feeder bay will be required at Gravir substation. | Pentland Road Windfarm Ltd | Stornoway | Pentland Road
SHETL-RI-058 | Reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe (Cambusmore) 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include two new Super Grid Transformers to connect Shin 132kV substation, new double circuit steel lattice tower L3/1 construction approximately 40km and works Beauly and Loch Buidhe 275kV substations. | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
|  | Innogy Renewables UK Ltd | Mybster 132/33kV | Bad a Cheo Wind Farm
|  | SSE Generation Ltd | Strathy North and Strathy South 132/33kV Substation | Strathy North and South Wind | 12/06/2015
|  | E.ON Climate & Renewables UK Developments Limited | Strathy Wood | Strathy Wood | 31/10/2021
|  | SSE Generation Ltd | Gordonbush | Gordonbush Wind | 31/10/2022
SHETL-RI-060 | Reconductor the west side of the 275kV circuit double circuit between Loch Buidhe and Dounreay (LT1/TD1/DU1) making it the same specification as the east side (LY2/YU2). | Infinergy Ltd | Limekilns 132/33kV substation | Limekilns
|  | Innogy Renewables UK Ltd | Mybster 132/33kV | Bad a Cheo Wind Farm
|  | SSE Generation Ltd | Strathy North and Strathy South 132/33kV Substation | Strathy North and South Wind | 12/06/2015
|  | E.ON Climate & Renewables UK Developments Limited | Strathy Wood | Strathy Wood | 31/10/2021
|  | SSE Generation Ltd | Gordonbush | Gordonbush Wind | 31/10/2022
SHETL-RI-061 | Establish a new 132kV double busbar substation near Dunvegan on Skye and construct a new 132kV single circuit line Trident arrangement approximately 150km back to Fort Augustus 132kV busbar. | Kilmac Energy | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm
SHETL-RI-062 | An HVDC switching station is required to integrate the Caithness - Moray transmission reinforcement and the Shetland connection. The HVDC switching station is proposed to be in the vicinity of Sinclair's Bay in Caithness. The HVDC switching station works will integrate with the Caithness - Moray transmission reinforcement and the Shetland HVDC link. | Peel (Yell) Wind Farms Limited | Yell | Beaw Field Wind Farm
|  | SCT Renewables Limited | Kergord | Viking Wind Farm
SHETL-RI-064 | Develop the existing Fort Augustus substation to include a new 400kV and 132kV busbar. The 400kV busbar is connected to the 132kV busbar via four 240MVA 400/132kV supergrid transformers. | SSE Generation Ltd | Coire Glas | Coire Glas Pumped Storage | 31/10/2025
|  | Kilmac Energy | Glen Ullinish 132/33kV Substation | Glen Ullinish Wind Farm
SHETL-RI-068 | Upgrade the existing 132kV double circuit OHL between Fort Augustus and Invergarry substation by a new 400kV OHL. The existing 132kV OHL forms part of the Fort Augustus to Fort William FFE/FFW circuits. Part of the upgrade is to establish a 400/132kV substation at Invergarry to connect the existing 132kV OHL from Fort William and Invergarry Generation. The new 400kV OHL will terminate into the 400kV busbar at For Augustus. | SSE Generation Ltd | Coire Glas | Coire Glas Pumped Storage | 31/10/2025
SHETL-RI-069 | A Static VAR Compensators (SVC) is required at Tummel Bridge for voltage support on the 275kV Beauly-Denny overhead line. The SVC will have a capability of +225MVAr and -75MVAr. Extend the 275kV busbar at Tummel bridge to accommodate the SVC. | SSE Generation Ltd | Coire Glas | Coire Glas Pumped Storage | 31/10/2025
|  | SSE Generation Ltd | Stronelairg 132/33kV Substation | Stronelairg | 31/03/2017
SHETL-RI-071 | Establish 132kV transmission infrastructure between a new 132kV busbar on South Ronaldsay, Orkney and a new 132kV double busbar arrangement at Marwick Head on Orkney. The new 132kV infrastructure will be routed via Kirkwall to allow for provision of a new GSP near Kirkwall in the future. | Brims Tidal Array Limited | Bay of Skaill 132/33kV substation | Cantick Head
SHETL-RI-072 | Replace the existing 55km XH1/XH2 275kV double circuit OHL with a 400kV double circuit OHL. The new 400kV OHL will terminate on the 400kV busbars at Blackhillock and Kintore substations. | Vattenfall Wind Power Ltd | Cairnford | Clashindarroch 2
SHETL-RI-073 | Keith MacDuff Blackhillock 132kV Reinforcement - Reinforce the existing Keith, Macduff and Blackhillock 132kv transmission network by reconfiguring the transmission circuits away from Keith 132kV substation and increasing the supergrid capacity at Blackhillock substation. | Paul's Hill II Limited | Glenfarclas 132/33kV Substation | Paul's Hill II Wind Farm | 31/10/2021
|  | Elgin Energy EsCo Limited | Elgin | Milltown Airfield Solar Farm | 31/10/2020
|  | Elgin Energy EsCo Limited | Elgin | Speyslaw Solar | 31/10/2020
SHETL-RI-074 | Established a new 400kV double busbar arrangement close to New Deer in Aberdeenshire. The proposed New Deer substation is located west of Peterhead along the existing 275kV double circuit OHL between Peterhead and Blackhillock/Keith/Kintore (VH & VX1 circuits). Establish a new ten bay 400kV double busbar arrangement complete with one bus section, two bus couplers and busbar selections on all circuits. The 275kV OHL is proposed to be reinsulated to 400kV between Peterhead and Rothienorman. The project will be completed in two stages . The 400kV double busbar will be built with a 400/275kV transformer connected between each side of the double busbar. The bus couplers shall be run open and locked, resulting in one side of the double busbar operating at 400kV, with the other side operating at 275kV. The transformer will be re-utilised at Peterhead in the final 400kV configuration. | Moray Offshore Renewables Ltd | Moray Firth 220/33kV Platform 1 & 2 Offshore Substation | Moray Firth Offshore Wind Farm | 01/07/2019
SHETL-RI-075A | Establishment of the first 132kV transmission corridor on Orkney between Bay of Skaill and the new Finstown 132kV Busbar. | Westray South Tidal Development Limited | Crook 132/33kV Substation | Westray South
SHETL-RI-075B | Establishment of a 132kV Busbar at Crook and connection to Finstown substation via a 132kV Trident OHL. | Westray South Tidal Development Limited | Crook 132/33kV Substation | Westray South
SHETL-RI-075C | The establishment of a second 132kV OHL trident line between Bay of Skaill substation and Finstown substation. | Westray South Tidal Development Limited | Crook 132/33kV Substation | Westray South
SHETL-RI-075D | The establishment of a 132 kV trident OHL between Bay of Skaill (SHETL-RI-19) and the Crook 132 kV Busbar. Works will also include conversion of Crook 132 kV busbar to double busbar arrangement, and the installation of a 200 MVA quad booster with a bypass on the Finstown-Crook 132 kV circuit at Crook. | Westray South Tidal Development Limited | Crook 132/33kV Substation | Westray South
SHETL-RI-077 & SPT-RI-150 | Establish a third 240MVA 220kV subsea cable circuit between Crossaig 132kV Substation and Hunterston 400kV Substation. | Good Energy Development (No.7) Limited | Willow Wind 132/33kV | Willow Wind Farm | 01/04/2023
|  | RES UK & Ireland Limited | Carradale | Blary Hill Wind Farm
SHETL-RI-079 | Reinforce the transmission network between Blackhillock and Aberlour (near Dufftown) by replacing part of the existing Glenfarcles - Keith (FK Circuit) 132kV OHL. It is proposed to replace the existing 132kV OHL with a new 275kV double circuit OHL. | Elchies Wind Limited | Elchies 132/33kV Substation | Elchies Wind Farm
SHETL-RI-084 | Upgrade the capacity of the 132kV double circuit OHL between Carradale and Crossaig to 334MVA summer pre-fault rating using Araucaria conductor operated at 85°C. | RES UK & Ireland Limited | Carradale | Blary Hill Wind Farm
|  | Fyne Futures Limited | Carradale 132/33kV Substation | Auchadaduie Wind Farm | 31/03/2017
SHETL-RI-085 | Establish a new 400/132kV Substation at Melgarve to allow the connection of wind generation in the area. | SSE Generation Ltd | Stronelairg 132/33kV Substation | Stronelairg | 31/03/2017
SHETL-RI-089 | Upgrade the 120MVA 275/132kV SGT1 at Farigaig substation to a 240MVA SGT to facilitate the connection of generation in the area. | Aberarder Wind Farm LLP | Aberarder 132/33Kv Substation | Aberarder Wind Farm | 30/06/2020
SHETL-RI-092 | Establish a new 132kV cable circuit between Melgarve substation and a new 132kV busbar at Stronelairg. | SSE Generation Ltd | Stronelairg 132/33kV Substation | Stronelairg | 31/03/2017
SHETL-RI-098 | Dunoon GL1-GL2 OHL Circuit Reconductoring — Reconductor approximately 17km of double circuit overhead line between Dunoon substation and the SHET – SPT boundary. Both sides of the double circuit OHL (GL1 and GL2) is to be reconductored | Infinergy Ltd |  | Ardtaraig Wind Farm | 31/10/2021
SHETL-RI-099 | Reconfigure the 132kV substation at Keith by installing a new 132kV busbar and connecting the Macduff circuits, the future Ault more circuit and relocating the existing Keith GT1 and GT3 to the new busbar. The new busbar at Keith will interface with the Keith - Macduff - Blackhillock project. | Elgin Energy EsCo Limited | Elgin | Milltown Airfield Solar Farm | 31/10/2020
|  | Elgin Energy EsCo Limited | Elgin | Speyslaw Solar | 31/10/2020
SHETL-RI-106 | Connagil 2nd SGT - At Connagill substation, install a 2nd 275/132kV 360MVA supergrid transformer, to enable the connection of wind generation in the local area to the Dounreay – Loch Buidhe 275kV circuit.. | E.ON Climate & Renewables UK Developments Limited | Strathy Wood | Strathy Wood | 31/10/2021
SHETL-RI-109 | Loch Buidhe — Spittal 132kv Reconductoring - Reconductor the existing 90km 132kV tower line between Loch Buidhe and Spittal substations. The 132kV overhead line is to be reconductored with a higher capacity conductor than the existing conductor, and should have a minimum summer pre4ault rating of 176MvA. | E.ON Climate & Renewables UK Developments Limited | Golticlay 132/33kV | Golticlay Wind Farm | 31/10/2022
|  | Green Cat Renewable Developments Ltd | Brora GSP | Navidale Wind Farm | 31/10/2021
SHETL-Rl-007c | Blackhillock Substation Redevelopment - Redevelop Blackhillock Substation to enable the construction of a new 400kv, 275kV and 132kV double busbars. Connectivity is maintained by 2 x 1200MVA 400/275kV SGTs and 2 x 24GMVA 275/132kv SGTs. Connect the existing 2 x 24OMVA 275/132kv SGTs at Keith to Blackhillock 275kV busbar using 275kV Cables. | E.ON Climate & Renewables UK Developments Limited | Golticlay 132/33kV | Golticlay Wind Farm | 31/10/2022
SHETL-Rl-032a | Dounreay Spittal 275kV & 132kV OHL Reinforcement - A new 275 kV overhead line and substation works between Dounreay,Thurso and Spittal Substations.( | E.ON Climate & Renewables UK Developments Limited | Golticlay 132/33kV | Golticlay Wind Farm | 31/10/2022
SHETL-Rl-035 | Loch Buidhe 275/132kV New Substation - Construct a new 275/132kv substation near Loch Buidhe, at the crossing point of the existing Beauly-Dounreay 275kv and Shin-Mybster 1 32kV double circuit overhead lines. Established a new 275kV and 132kV double busbar arrangement and turn in the existing 275kv Beauly-Dounreay and 132kV Shin-Mybster double circuit overhead lines complete with associated circuit breakers and disconnectors. Connect the new 275kv double busbar to the new 132kv double busbar via two 24OMVA 275/132kV SGTs. | E.ON Climate & Renewables UK Developments Limited | Golticlay 132/33kV | Golticlay Wind Farm | 31/10/2022
SHETL-Rl-058 | Beauly-Loch Buidhe 275kV OHL Reinforcement (Rebuild) - This project is to reinforce the existing BSW/BSE Beauly, Shin to Loch Buidhe (Cambusmore) 132kV double circuit with a higher capacity 275kV double circuit OHL. The reinforcement will include: (a). Two new Super Grid Transformers to connect Shin 132kV substation. (b). New double circuit steel lattice tower L3/1 construction approximately 40km. (c). Works at Beauly and Loch Buidhe 275kV substations. | E.ON Climate & Renewables UK Developments Limited | Golticlay 132/33kV | Golticlay Wind Farm | 31/10/2022
SHETL-Rl-060 | Loch Buidhe/Dounreay 275kv Circuit (DU1) Reconductoring | E.ON Climate & Renewables UK Developments Limited | Golticlay 132/33kV | Golticlay Wind Farm | 31/10/2022
SHET-RI-043 | Lewis Infrastructure - Build a new 132kV single circuit OHL between Arnish substation, and the Muaitheabhal Tee point. Dismantle the existing 132kV single circuit OHL between Stornoway Tee point, and the Muaitheabhal Tee point. | EDF Energy Renewables Limited | Muaitheabhal 132/33kV Substation | Muaitheabhal Wind Farm
SHET-RI-069 | Tummel SVC – Installation of a Static VAR Compensator (SVC) at Tummel substation for voltage support on the 275kV Beauly-Denny overhead line. (SHET-RI-069) | Simec Lochaber Hydropower 2 Limited | Glenshero | Glenshero | 31/05/2022
SHET-RI-085 | Melgarve 400/132kV Substation – Establish a new 400/132 kV Substation at Melgarve, to allow the connection of wind generation in the area. (SHET-RI-085) | Simec Lochaber Hydropower 2 Limited | Glenshero | Glenshero | 31/05/2022
SHET-RI-105 | Establish a new double busbar at Rothienorman to be built at 400kV, but initially operate at 275kV. Re-conductor the 275kV double circuit overhead line between the new double busbar at Rothienorman and Kintore substation. | MORAY OFFSHORE WINDFARM (WEST) LIMITED | Moray Firth 220/33kV Platform 1 & 2 Offshore Substation | Moray Offshore West Windfarm | 31/03/2024
|  | Moray Offshore Renewables Ltd | Moray Firth 220/33kV Platform 1 & 2 Offshore Substation | Moray Firth Offshore Wind Farm | 01/07/2019
SHET-RI-106a | Gordonbush Circuit Transfer - Transfer the connection of Gordonbush windfarm from the TD1 (West) 275kV circuit to the BNG2 (East) 275kV circuit to balance the power flows on the associated overhead line between Loch Buidhe and Dounreay. A new 275kV circuit breaker and line disconnectors are to be installed on the 275kV BNG2 (East) circuit, on the Connagill side of the new Gordonbush connection point. The existing line disconnectors will be dismantled and removed from the TD1 circuit. | SSE Generation Ltd | Gordonbush | Gordonbush Wind | 31/10/2022
Sneddon Law Item 1 | Installation and commissioning of a protection scheme to interface with the relevant transmission licensee's protection scheme(s) identified in one off works and relay a signal to the user's wind farm substation in order to disconnect the user's wind farm. These works will need to be completed by the host distribution network operator. | Sneddon Law Community Wind Company Limited | Kilmarnock Town 275/33kV | Sneddon Law Wind | 31/10/2018
Speyside CHP item 1 | Install a fourth 90MVA 132/33kV Grid Transformer, 1 x 132kV circuit breaker bay and 1 x 33kV transformer incomer circuit breaker at the Keith Grid Supply Point Substation. | Speyside Renewable Energy Partnership Ltd | Keith 132/33kV | Speyside CHP
SPT-RI-007 | Extend the 275kV overhead line network in Ayrshire from Coylton 275kV substation to the west of New Cumnock. Construct New Cumnock (Meiklehill) 275kV/132kV substation. New Cumnock (Meiklehill) 132kV substation will form a 'collector' substation for renewable generation in south and east Ayrshire. Extension of 132kV network from New Cumnock 132kV substation is subject of separate TO Reinforcement Instruction. | E.ON Climate & Renewables UK Developments Limited | Enoch Hill 132/33kV | Enoch Hill | 30/11/2020
|  | Whiteside Hill Windfarm (Scotland) Limited | Coylton | Whiteside Hill Wind Farm
|  | Sanquhar II Community Wind Company Limited |  | Sanquhar IIa Community Wind Farm | 30/11/2023
|  | AFTON WIND FARM LIMITED | Afton | Afton | 30/06/2017
|  | Longburn Wind Farm Limited |  | Long Burn Wind Farm
|  | Glenmuckloch Renewable Energy Limited | Glenmuckloch 33kV | Glenmuckloch Wind Farm | 30/08/2022
|  | E.ON Climate & Renewables UK Developments Limited | Lorg Wind Farm 132/32kV | Lorg Wind Farm | 15/11/2022
|  | Blackcraig Wind Farm (Scotland) Limited | Black Craig | Blackcraig Wind Farm
|  | Brockloch Rig Windfarm Ltd | Dun Hill 132/33kV Substation | Windy Standard II (Brockloch Rig 1) Wind Farm | 30/04/2017
|  | Pencloe Wind Energy Ltd | Pencloe 132/33kV | Pencloe Windfarm
|  | Sandy Knowe Wind Farm Ltd | Glenglass 132/33kv | Sandy Knowe Wind Farm | 30/10/2021
|  | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV | Sanquhar II Wind Farm
|  | Vattenfall Wind Power Ltd | New Cummock 132/33kV | South Kyle | 01/06/2019
|  | Sanquhar Community Wind Company Limited | Ulzieside 132/33kV | Sanquhar Wind Farm | 02/10/2020
|  | Brockloch Rig III Limited | Dun Hill | Windy Standard III Wind Farm | 30/11/2019
SPT-RI-017 | Construction of a single circuit 132kV overhead line (15km) and single cable circuits (1km) from Gretna substation, heading north, to a wind farm site. These works will be required in response to new generation connections in the vicinity of Gretna. | Crossdykes Wind Farm Limited | Crossdykes 33kV Substation | Crossdykes | 31/10/2018
SPT-RI-017 | Construction of a single circuit 132kV overhead line (15km) and single cable circuits (1km) from Gretna substation, heading north, to a wind farm site. These works will be required in response to new generation connections in the vicinity of Gretna. | Hopsrig Wind Farm Limited | Hopsrig Wind Farm 132/33kV Substation | Hopsrig Wind Farm | 30/10/2021
SPT-RI-022 | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | Glenmuckloch Renewable Energy Limited | Glenmuckloch 33kV | Glenmuckloch Wind Farm | 30/08/2022
SPT-RI-022 | Construction of a double circuit 132kV overhead line (approx. 14km) from Black Hill Collector Substation heading east to 132kV Glenglass Collector Substation. Glenglass substation will incorporate two 132/33kV 120MVA transformers and 33kV switchboard (single busbar) with a bus-section. | Whiteside Hill Windfarm (Scotland) Limited | Coylton | Whiteside Hill Wind Farm
|  | Glenmuckloch Renewable Energy Limited | Glenmuckloch 33kV | Glenmuckloch Wind Farm | 30/08/2022
|  | Sandy Knowe Wind Farm Ltd | Glenglass 132/33kv | Sandy Knowe Wind Farm | 30/10/2021
|  | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV | Sanquhar II Wind Farm
|  | Sanquhar Community Wind Company Limited | Ulzieside 132/33kV | Sanquhar Wind Farm | 02/10/2020
SPT-RI-028 | Reconfigure and extend Dalmally 275kV substation to a double busbar arrangement. Associated civil works and other miscellaneous works, including installation/modification of associated protection, control, telecommunications and metering equipment and modification of the Operation Tripping Scheme associated with the connection of Inveraray 275kV Substation. | SSE Renewables Developments (UK) Ltd | Carradale | Tangy III Wind Farm | 01/04/2022
SPT-RI-034 | A 132/33kV substation will be established adjacent to Margree wind farm, near St Johns Town of Dalry, in Dumfries and Galloway. The substation will be connected to a new 132kV circuit from New Cumnock 275/132kV substation. It will provide a local 33kV point of connection for Margree wind farm (70.0MW), connection for a 33kV circuit to Loch Hill wind farm (27.5MW) and connection for 132kV circuit to Blackcraig wind farm (71.3MW). | Margree Wind Energy Limited | Margree 132/33kV Substation | Margree
SPT-RI-101 | Construct double circuit 132kV overhead line from New Cumnock 132kV substation to the new Windy Standard Collector Substation and at New Cumnock establish two new 132kV circuit breaker bays to facilitate the connection of the new circuits. | Aberdeen Offshore Wind Farm Limited | Blackdog 132kV Substation | Aberdeen Offshore Wind Farm | 01/04/2018
SPT-RI-101 | Construct double circuit 132kV overhead line from New Cumnock 132kV substation to the new Windy Standard Collector Substation and at New Cumnock establish two new 132kV circuit breaker bays to facilitate the connection of the new circuits. | Whiteside Hill Windfarm (Scotland) Limited | Coylton | Whiteside Hill Wind Farm
SPT-RI-111 | The Kendoon to Maybole T 132kV single circuit will be reconfigured to form two new circuits, a circuit from Kendoon to New Cumnock, and a circuit from New Cumnock to Margree windfarm substation. | Longburn Wind Farm Limited |  | Long Burn Wind Farm
|  | E.ON Climate & Renewables UK Developments Limited | Lorg Wind Farm 132/32kV | Lorg Wind Farm | 15/11/2022
|  | Margree Wind Energy Limited | Margree 132/33kV Substation | Margree
|  | Blackcraig Wind Farm (Scotland) Limited | Black Craig | Blackcraig Wind Farm
SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV Meikle Hill Collector Substation, heading east to 132kV Dun Hill Substation. These works will be required in response to new generation connections in the vicinity of Dun Hill substation. | Whiteside Hill Windfarm (Scotland) Limited | Coylton | Whiteside Hill Wind Farm
|  | AFTON WIND FARM LIMITED | Afton | Afton | 30/06/2017
|  | Brockloch Rig Windfarm Ltd | Dun Hill 132/33kV Substation | Windy Standard II (Brockloch Rig 1) Wind Farm | 30/04/2017
|  | Pencloe Wind Energy Ltd | Pencloe 132/33kV | Pencloe Windfarm
|  | Sandy Knowe Wind Farm Ltd | Glenglass 132/33kv | Sandy Knowe Wind Farm | 30/10/2021
|  | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV | Sanquhar II Wind Farm
|  | Sanquhar Community Wind Company Limited | Ulzieside 132/33kV | Sanquhar Wind Farm | 02/10/2020
|  | Brockloch Rig III Limited | Dun Hill | Windy Standard III Wind Farm | 30/11/2019
SPT-RI-114 | Construction of a double circuit 132kV steel tower line (approx. 15km) from 132kV Meikle Hill Collector Substation, heading east to 132kV Dun Hill Substation. These works will be required in response to new generation connections in the vicinity of Dun Hill substation. | Glenmuckloch Renewable Energy Limited | Glenmuckloch 33kV | Glenmuckloch Wind Farm | 30/08/2022
SPT-RI-115 | Construction of a double circuit 132kV steel tower line (approx. 1.5km) from 132kV Dun Hill substation heading east to 132kV Black Hill Substation. Black Hill substation will include three new 132kV circuit breakers (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | Whiteside Hill Windfarm (Scotland) Limited | Coylton | Whiteside Hill Wind Farm
|  | AFTON WIND FARM LIMITED | Afton | Afton | 30/06/2017
|  | Glenmuckloch Renewable Energy Limited | Glenmuckloch 33kV | Glenmuckloch Wind Farm | 30/08/2022
|  | Pencloe Wind Energy Ltd | Pencloe 132/33kV | Pencloe Windfarm
|  | Sandy Knowe Wind Farm Ltd | Glenglass 132/33kv | Sandy Knowe Wind Farm | 30/10/2021
|  | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV | Sanquhar II Wind Farm
|  | Sanquhar Community Wind Company Limited | Ulzieside 132/33kV | Sanquhar Wind Farm | 02/10/2020
SPT-RI-116A | Construction of Black Hill 132.33kV Substation including two 132kV circuit breakers (double busbar), two 132/33kV 90MVA transformers and 33kV B switchboard (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | AFTON WIND FARM LIMITED | Afton | Afton | 30/06/2017
SPT-RI-116B | Construction of Black Hill 132/33kV Substation including two 132kV circuit breakers (double busbar), two 132/33kV 90MVA transformers and 33kV B switchboard (double busbar). These works will be required in response to new generation connections in the vicinity of Black Hill Substation. | Pencloe Wind Energy Ltd | Pencloe 132/33kV | Pencloe Windfarm
SPT-RI-123 | Construction of Hunterston East 400kV Substation. These works are included as a part of the Western HVDC link project. | ScottishPower Renewables (UK) Limited | Carradale 132/33kV Substation | Beinn an Tuirc 3
SPT-RI-124 | A new 21 bay 400kV GIS substation in a 'Breaker and a Half' configuration will be installed at a site yet to be determined in the Torness area of East Lothian. Four existing SPT 400kV circuits will be connected to the new 400kV substation to provide connection to the wider transmission system. | Seagreen Wind Energy Ltd | Tealing 275/33kv | Firth of Forth Offshore Wind Farm 1A | 30/06/2019
|  | Seagreen Wind Energy Ltd |  | Firth of Forth Offshore Wind Farm 2A East & 2A West
|  | Seagreen Wind Energy Ltd | Branxton 400kV | Firth of Forth Offshore Wind Farm 2B East & 2B West
SPT-RI-130 | The overhead line conductor system on the existing 11.6km 400kV double circuit route from Strathaven to Wishaw (XH route) will be replaced with a conductor system of increased thermal rating. The overhead line conductor system on the existing 61.8km 400kV double circuit route from Wishaw to Smeaton (XJ route) will be replaced with a conductor system of increased thermal rating. The existing XH and XJ overhead line routes are equipped with twin 400mm² ACSR (Zebra) conductor operating at 65°C. The replacement conductor system is subject to ongoing consideration. These works will not modify the prevailing circuit configuration. | Seagreen Wind Energy Ltd | Branxton 400kV | Firth of Forth Offshore Wind Farm 2B East & 2B West
SPT-RI-131 | The overhead line conductor system on the existing 34.3km 400kV double circuit route from Eccles to the Branxton sealing end compound (ZT route) will be replaced with a conductor system of increased thermal rating. The existing ZT overhead line route is equipped with twin 700mm² AAAC (Araucaria) conductor operating at 75°C. While the replacement conductor system is subject to ongoing consideration, it is assumed at this time to be twin 2 x 620mm² Matthew GZTACSR. The existing disconnectors at Eccles 400kV Substation on the Branxton (Torness) and Sella West/Blyth circuits will be replaced in order to increase circuit thermal ratings. These works will not modify the prevailing circuit configuration. | Seagreen Wind Energy Ltd | Branxton 400kV | Firth of Forth Offshore Wind Farm 2B East & 2B West
SPT-RI-136 | Reconductor the 275kV single circuit overhead line (YY route) between Coylton 275kV substation and Mark Hill 275kV substation. | Chirmorie Wind Farm Limited |  | Chirmorie Wind Farm | 31/10/2022
|  | PNE Wind UK Ltd | Tralorg 33KV | Tralorg Wind Farm
SPT-RI-137 | Currently there is ~161MW contracted at Dunbar Grid Supply Point. In order to provide firm capacity for the generations, it is proposed to reinforce the Torness/Innerwick/Dunbar No.1 and No 2 132kV circuits, consisting of tower lines and underground cables to provide a minimum pre-fault summer rating of 160MVA per circuit. For the overhead line section, it is anticipated that the existing towers are not suitable for reconductoring to achieve the proposed rating hence a rebuilding of the tower lines is required. It is also proposed to reinforce the existing 132kV busbars/isolators at Innerwick 132kV substation to accommodate the minimum rating of 160MVA of the reinforced circuits. | Viridor Enviroscot Limited | Dunbar | Dunbar ERF | 31/10/2021
SPT-RI-141 | The South West area of Scotland is an area rich in renewable energy resources such as onshore wind, offshore wind, hydro and marine. The network is primarily a legacy 132kV active and interconnected system which, along with the 275kV Auchencrosh circuit, is fully committed in terms of generation connections. It is proposed to establish a new 275kV supergrid infrastructure with a reduced 132kV radal network operating as local collector and supply hubs. The aim will be to extend the 275kV network from Harker to Auchencrosh to provide much needed additional capacity to the area for the connection of renewable generation. | Willowind Gass Limited | Newton Stewart | Gass Wind Farm | 30/10/2023
|  | Partnerships for Renewables Development | Chapelcross 132/33kV Substation | Craig II Wind Farm
SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | E.ON Climate & Renewables UK Developments Limited | Enoch Hill 132/33kV | Enoch Hill | 30/11/2020
|  | Sanquhar II Community Wind Company Limited |  | Sanquhar IIa Community Wind Farm | 30/11/2023
|  | Glenmuckloch Pumped Storage Limite | Glenmuckloch 132kV Substation | Glenmuckloch Pumped Storage | 30/11/2022
|  | Longburn Wind Farm Limited |  | Long Burn Wind Farm
|  | E.ON Climate & Renewables UK Developments Limited | Lorg Wind Farm 132/32kV | Lorg Wind Farm | 15/11/2022
|  | Chirmorie Wind Farm Limited |  | Chirmorie Wind Farm | 31/10/2022
|  | Pencloe Wind Energy Ltd | Pencloe 132/33kV | Pencloe Windfarm
|  | Sandy Knowe Wind Farm Ltd | Glenglass 132/33kv | Sandy Knowe Wind Farm | 30/10/2021
|  | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV | Sanquhar II Wind Farm
|  | Vattenfall Wind Power Ltd | New Cummock 132/33kV | South Kyle | 01/06/2019
|  | Kirk Hill Wind Farm Limited | Maybole | Kirk Hill | 30/09/2022
|  | EDF Energy Renewables Limited | Stranoch Wind 132/33KV | Stranoch Wind Farm | 31/10/2017
|  | PNE Wind UK Ltd | Tralorg 33KV | Tralorg Wind Farm
|  | Sanquhar Community Wind Company Limited | Ulzieside 132/33kV | Sanquhar Wind Farm | 02/10/2020
|  | Brockloch Rig III Limited | Dun Hill | Windy Standard III Wind Farm | 30/11/2019
SPT-RI-142 | The 275kV double circuit between Kilmarnock South and Coylton, XY route is approximately 15.5km in length and existing overhead line circuits are twin Zebra 2 x 400m² ACSR with a pre-fault summer rating of 640MVA. The Kilmarnock South - Coylton No.1 circuit also has a cable section at Chipperlaigen which has a maximum winter post fault rating 710MVA. To accommodate the generation in South West Scotland it is proposed to uprate the Kilmarnock South - Coylton 275kV circuits by replacing the overhead line with twin ACCR (Aluminium Conductor Composite Reinforced) operating at temperatures of up to 210°C. The Chipperlaigen cable will be replaced with a gas insulated busbar arrangement. It is expected that a 1600MVA minimum pre-fault continuous rating will be achieved with ACCR conductor. | Glenmuckloch Renewable Energy Limited | Glenmuckloch 33kV | Glenmuckloch Wind Farm | 30/08/2022
SPT-RI-143 | The existing switchgear in Kilmarnock South 275kV substation is rated at 2000Amps/952MVA and this will need to be replaced with higher rated switchgear to ensure thermal limits are not exceeded at the 275kV substation. | E.ON Climate & Renewables UK Developments Limited | Enoch Hill 132/33kV | Enoch Hill | 30/11/2020
|  | Sanquhar II Community Wind Company Limited |  | Sanquhar IIa Community Wind Farm | 30/11/2023
|  | Glenmuckloch Pumped Storage Limite | Glenmuckloch 132kV Substation | Glenmuckloch Pumped Storage | 30/11/2022
|  | Longburn Wind Farm Limited |  | Long Burn Wind Farm
|  | Glenmuckloch Renewable Energy Limited | Glenmuckloch 33kV | Glenmuckloch Wind Farm | 30/08/2022
|  | E.ON Climate & Renewables UK Developments Limited | Lorg Wind Farm 132/32kV | Lorg Wind Farm | 15/11/2022
|  | Chirmorie Wind Farm Limited |  | Chirmorie Wind Farm | 31/10/2022
|  | Sandy Knowe Wind Farm Ltd | Glenglass 132/33kv | Sandy Knowe Wind Farm | 30/10/2021
|  | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV | Sanquhar II Wind Farm
|  | Kirk Hill Wind Farm Limited | Maybole | Kirk Hill | 30/09/2022
|  | EDF Energy Renewables Limited | Stranoch Wind 132/33KV | Stranoch Wind Farm | 31/10/2017
|  | PNE Wind UK Ltd | Tralorg 33KV | Tralorg Wind Farm
|  | Sneddon Law Community Wind Company Limited | Kilmarnock Town 275/33kV | Sneddon Law Wind | 31/10/2018
|  | Brockloch Rig III Limited | Dun Hill | Windy Standard III Wind Farm | 30/11/2019
SPT-RI-144 | At Coalburn 400/132kV substation an additional 240MVA 400/132kV transformer (SGT3) will be installed. | Brookfield Renewable UK Ltd | Kennoxhead | Kennoxhead Wind Farm | 31/10/2023
|  | Banks Renewables (Harting Rig Wind Farm) Limited | Harting Rig 132/33kv | Harting Rig Wind Farm | 30/07/2020
|  | Banks Renewables Limited | Middle Muir 132/33kV | Middle Muir Wind Farm | 30/05/2018
|  | 3R Energy Solutions | Coalburn132/33kV | Douglas West | 31/10/2021
|  | Cumberhead Wind Energy Limited | Cumberhead | Cumberhead | 20/10/2019
SPT-RI-145 | Construction of Dun Hill 132/33kV Substation including three 33kV circuit breakers, two 132/33kV 90MVA transformers and 33kV switchboard (double busbar). These works will be required in response to new generation connections in the vicinity of Dun Hill Substation. | Brockloch Rig Windfarm Ltd | Dun Hill 132/33kV Substation | Windy Standard II (Brockloch Rig 1) Wind Farm | 30/04/2017
|  | Brockloch Rig III Limited | Dun Hill | Windy Standard III Wind Farm | 30/11/2019
SPT-RI-146 | To accommodate the generation at Maybole GSP it is proposed to construct a new 132kV L7 double circuit tower line between Maybole and Coylton 132kV substations, with each circuit having a minimum summer pre-fault continuous rating of 150MVA. The existing 132kV overhead line circuits between Maybole and Coylton will be dismantled. | Kirk Hill Wind Farm Limited | Maybole | Kirk Hill | 30/09/2022
SPT-RI-147 | A new 275kV double circuit overhead line will be constructed between Kilmarnock South and Coylton 275kV substation having a minimum summer pre-fault rating 1500MVA per circuit. In addition, the existing 132V circuit between Kilmarnock South and the Coylton T will be removed to facilitate a line routing for the third Kilmarnock South to Coylton 275kV circuit. Moreover, the Coylton 275/132kV SGT1 and SGT2 120MVA transformers will be replaced with 240MVA units to provide sufficient export capacity for the contracted generation in the area. | RES UK & Ireland Limited | Glenluce | Glenchamber Wind Farm | 30/04/2023
|  | Chirmorie Wind Farm Limited |  | Chirmorie Wind Farm | 31/10/2022
|  | Kirk Hill Wind Farm Limited | Maybole | Kirk Hill | 30/09/2022
|  | PNE Wind UK Ltd | Tralorg 33KV | Tralorg Wind Farm
SPT-RI-154 | There are currently ~102MW contracted at Glenluce GSP and a further 34.5MW (Annabaglish WF) is expected to accept their offer to connect. The amount of generation has reached a level where the thermal rating of 132kV double circuit between Glenluce and Newton Stewart is exceeded (currently 86MVA, Summer) and these circuits are therefore required to be uprated and to ensure compliance with the NETS SQSS. The existing two 132kV circuits between Glenluce and Newton Stewart are on double circuit tower lines and 132kV underground sections (For the overhead line termination at Newton Stewart end). The entire circuit route consists of BT Route (22km), towards Newton Stewart. These overhead line circuits are single 175mm² ACSR with a pre-fault summer rating of 86MVA. The total length of the entire circuit is ~22km. It is proposed to reconductor the 132kV circuits with 200mm² Poplar AAAC conductor on the existing double circuit tower lines between Glenluce and Newton Stewart. The new circuit will provide the following circuit ratings: 124MVA (Summer), 134MVA (Autumn) and 140 (Winter) pre-fault. | RES UK & Ireland Limited | Glenluce 132/33kV | Annabaglish | 31/10/2023
SPT-RI-155 | Replace the 3.2km 132kV undergroud cable section on the Coalburn to Linmill No.1 132kV circuit. | ILI (Strathaven South) Ltd | Linnmill Substation | Strathaven South Dedicated Line
|  | 3R Energy Solutions | Coalburn132/33kV | Douglas West | 31/10/2021
SPT-RI-158 | Contracted renewable generation South West Scotland has reached a level where the thermal uprating of the New Cumnock 275kV substation supergrid 275/132kV transformers, which connect to 132kV Board A is required. It is proposed to replace the 275/132kV SGT1A, SGT2A and SGT3A 240MVA auto wind transformers with 360MVA units. This will provide Board A with a firm capacity 720MVA and a non-firm capacity of 1080MVA. These works are dependent on the contracted generation position in South West Scotland as indicated in January 2014. | E.ON Climate & Renewables UK Developments Limited | Enoch Hill 132/33kV | Enoch Hill | 30/11/2020
|  | Sanquhar II Community Wind Company Limited |  | Sanquhar IIa Community Wind Farm | 30/11/2023
|  | Glenmuckloch Renewable Energy Limited | Glenmuckloch 33kV | Glenmuckloch Wind Farm | 30/08/2022
|  | Sandy Knowe Wind Farm Ltd | Glenglass 132/33kv | Sandy Knowe Wind Farm | 30/10/2021
|  | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV | Sanquhar II Wind Farm
SPT-RI-161 | Installation of an Energy Management (Overload Protection) Scheme at Chapelcross 132kV substation. The scheme will issue a signal to SPD and/or SPT to disconnect the appropriate generators if the pre-fault continuous rating of any of the following circuits is exceeded: Chapelcross to Harker 132kV circuit, Chapelcross to Gretna No1 132kV circuit and Chapelcross to Gretna No2 132kV circuit. | Partnerships for Renewables Development | Chapelcross 132/33kV Substation | Craig II Wind Farm
SPT-RI-162 | 9. Coylton 275kV Infrequent Infeed Loss Risk Protection - A protection scheme will be installed at Coylton 275kV substation, on the Ayr/Kilmarnock South No.1 and No.2 275kV circuits (XY Route), such that if a level of power flow from Coylton to Kilmarnock South is detected which may result in the Infrequent Infeed Loss Risk (as defined in the NETS Security and Quality of Supply Standard) being exceeded, a trip signal will be provided to the Relevant Transmission Licensee/or host Distribution Network Operator to disconnect generation as required such that the Infrequent Infeed Loss Risk is not exceeded. | E.ON Climate & Renewables UK Developments Limited | Enoch Hill 132/33kV | Enoch Hill | 30/11/2020
SPT-RI-164 | At Coalburn 400/132kV substation an additional 340MVA 400/132kV transformer (SGT4) will be installed. In addition a 400kV bus section circuit breaker will be installed on the Reserve busbar, and a second 400kV bus coupler circuit breaker will be installed on the Reserve busbar and a second 400kV bus coupler circuit breaker between the main and reserve busbars, along with a 400kV switchbay to connect SGT 5. The existing 132kV double busbar will be extended and split such SGT3 (Installed as part of TORI14) and SGT4 supply a separate section of 132kV double busbar (the B Board). On the B Board a 132kV feeder bay will be installed (for SGT4), a bus coupler 132kV circuit breaker and two 132kV switchbays (with associated 132kV cabling) to allow the transfer of two 132kV circuits from the A Board to the B Board as appropriate to the transformer capacity. This will increase the firm transformer capacity between the Coalburn 400kV and 132kV busbars to 600MVA (240MVA on Board A and 360MVA on Board B), to provide sufficient thermal capacity for the level of renewable generation contracted to connect o the Coalburn 132kV network. | Banks Renewables (Harting Rig Wind Farm) Limited | Harting Rig 132/33kv | Harting Rig Wind Farm | 30/07/2020
SPT-RI-168 | Installation of a protection scheme at Gretna 400/132kV substation. The scheme will issue a signal to the Host Distribution Network Operator to disconnect the appropriate generators if either SGT1 or SGT2 is overloaded or if both transformers are out of service (Following planned or unplanned outages). | Partnerships for Renewables Development | Chapelcross 132/33kV Substation | Craig II Wind Farm
SPT-RI-173 | There is currently 246MW (259MVA, including 132kV and 33kV connections) contracted at the proposed Glenglass 132kV substation. In order to facilitate the currently contracted 132kV generation connections at Glenglass 132kV substation, it is proposed to install a new 132kV eight bays (for two new wind farm connections), GIS double busbar at Glenglass. The new eight bays double busbar substation will provide two 132/33kV transformers, two 132kV incomers, one bus coupler and two 132kV circuit breakers for the contracted wind farms. | Sandy Knowe Wind Farm Ltd | Glenglass 132/33kv | Sandy Knowe Wind Farm | 30/10/2021
|  | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV | Sanquhar II Wind Farm
SPT-RI-176 | 10. New Cumnock Overload Protection Scheme - To utilise the non-firm capacity at New Cumnock and the 132kV network in South West Scotland an overload protection scheme is required at New Cumnock substation to monitor the loading on the 275kV circuits from Coylton, supergrid transformers and 132kV circuits at New Cumnock to prevent any overloading on the transmission system. The scheme at New Cumnock will communicate with remote systems at Dunhill, Blackhill, Glenglass and Kendoon North substations to trigger tripping signals to generators connected at these substations. | E.ON Climate & Renewables UK Developments Limited | Enoch Hill 132/33kV | Enoch Hill | 30/11/2020
|  | Sanquhar II Community Wind Company Limited |  | Sanquhar IIa Community Wind Farm | 30/11/2023
SPT-RI-180 | Coalburn SGTx Overload Protection Scheme: An overload protection scheme will be installed at Coalburn 400/132kV substation such that if SGT1 or SGT2 is overloaded, a trip signal will be issued to SPD at Linnmill GSP, and/or to SPT generation connected directly to Coalburn 132kV substation, to disconnect the appropriate generators to remove the overload. Following completion of Coalburn SGT3 (SPT-RI-144), this transformer will be added to the overload scheme proposed in this TORI (SPT-RI-180). | Cumberhead Wind Energy Limited | Cumberhead | Cumberhead | 20/10/2019
SPT-RI-186 | Installation of an overhead protection scheme at Kilmarnock South 400/275kV substation. | E.ON Climate & Renewables UK Developments Limited | Enoch Hill 132/33kV | Enoch Hill | 30/11/2020
|  | Sanquhar II Community Wind Company Limited |  | Sanquhar IIa Community Wind Farm | 30/11/2023
|  | Glenmuckloch Pumped Storage Limite | Glenmuckloch 132kV Substation | Glenmuckloch Pumped Storage | 30/11/2022
|  | RES UK & Ireland Limited | Glenluce 132/33kV | Annabaglish | 31/10/2023
|  | Longburn Wind Farm Limited |  | Long Burn Wind Farm
|  | Glenmuckloch Renewable Energy Limited | Glenmuckloch 33kV | Glenmuckloch Wind Farm | 30/08/2022
|  | E.ON Climate & Renewables UK Developments Limited | Lorg Wind Farm 132/32kV | Lorg Wind Farm | 15/11/2022
|  | Sandy Knowe Wind Farm Ltd | Glenglass 132/33kv | Sandy Knowe Wind Farm | 30/10/2021
|  | Sanquhar II Community Wind Company Limited | Sanquhar 132/33kV | Sanquhar II Wind Farm
|  | EDF Energy Renewables Limited | Stranoch Wind 132/33KV | Stranoch Wind Farm | 31/10/2017
SPT-RI-189 | A 132/33kV substation will be established adjacent to Ewe Hill Wind Farm, in Dumfries and Galloway. The substation will be connected to a new 132kV circuit from Gretna 400/132kV substation. It will provide a local 33kV point of connection for renewable generation from Ewe Hill and Crossdykes wind farms. This TORI describes the works required for the installation of a 90MVA, 132/33kV transformer at Ewe Hill Farm. | Crossdykes Wind Farm Limited | Crossdykes 33kV Substation | Crossdykes | 31/10/2018
SPT-RI-205 | Installation of approximately 1km of 132kV overhead line between Chirmorie Wind Farm substation and the tee point on the Mark Hill to Stranoch wind farm overhead line, a 132kV isolator at Chirmorie wind farm substation and 132kV substation at Mark Hill and a 132kV switch bay will be installed. From this a 132kV circuit consisting 0.5km of underground cable and 13.5 of 132kV overhead line 300mm UPAS conductor) will be installed to the overhead line tee point connecting the circuits to Chirmorie and Stranoch wind farms. | Chirmorie Wind Farm Limited |  | Chirmorie Wind Farm | 31/10/2022
|  | EDF Energy Renewables Limited | Stranoch Wind 132/33KV | Stranoch Wind Farm | 31/10/2017
SPT-RI-206 | At Mark Hill substation a 275kV switchbay will be installed to control a 275/132kV 240MVA transformer (SGT3). This will connect to a 132kV busbar (B Board) provided for the connection of renewable generation. | Chirmorie Wind Farm Limited |  | Chirmorie Wind Farm | 31/10/2022
|  | EDF Energy Renewables Limited | Stranoch Wind 132/33KV | Stranoch Wind Farm | 31/10/2017
SPT-RI-208 | An overload protection scheme will be installed at Chapelcross 132/33kV substation. The scheme will issue a trip signal to Host Distribution Network Operator to disconnect the appropriate generators if Grid T1 or Grid T2 is overloaded. | Partnerships for Renewables Development | Chapelcross 132/33kV Substation | Craig II Wind Farm
SPT-RI-213 | Installation of a third 275/132kV 240MVA transformer at New Cummock substation to increase the capacity of the 132kV Board B. | Glenmuckloch Pumped Storage Limite | Glenmuckloch 132kV Substation | Glenmuckloch Pumped Storage | 30/11/2022
|  | RES UK & Ireland Limited | Glenluce 132/33kV | Annabaglish | 31/10/2023
|  | Longburn Wind Farm Limited |  | Long Burn Wind Farm
|  | E.ON Climate & Renewables UK Developments Limited | Lorg Wind Farm 132/32kV | Lorg Wind Farm | 15/11/2022
SPT-RI-220 | New generation at SHETL’s Dunoon 132kV substation necessitates an uprating of the 132kV shared circuit between Dunoon and the tee into the Sloy-Windyhill circuit. SPT’s portion of the circuit runs between tower CM01 and mid span between CM13/14. The circuit presently uses 125mm2 ACSR Tiger conductor. It is proposed that SPT uprate the double circuit to Poplar 200mm2 conductor from CM1 to CM12. It is assumed SHETL will uprate over the boundary span between CM14 and CM13, terminating at tower CM12 | Infinergy Ltd |  | Ardtaraig Wind Farm | 31/10/2021
SPT-RI-221 | Extension of the 132kV double circuit between New Cumnock and Margree Tee to Glenlee substation. Modifications to the substation at Glenlee to form a six mesh corner arrangement to allow the termination of a new high capacity double circuit overhead line from New Cummock. | RES UK & Ireland Limited | Glenluce 132/33kV | Annabaglish | 31/10/2023
SPT-RI-222 | The works in this modernisation entails the construction of a new L4 (single POPLAR) 132kV double circuit from Glenlee to Tongland. This will enable the increase of transfer capability from Tongland to the wider supergrid system at New Cumnock and increase the local boundary capabilities of the 132kV system. The transfer capability of Tongland is currently limited by the single 132kV Lynx circuit between Glenlee and Dumfries and this scheme will remove this limitation. | Community Wind Power Ltd | Faw Side Community Wind Farm | Faw Side Community Wind Farm | 30/11/2024
SPT-RI-223 | Reconductor the existing circuits between Glenlee and Newton Stewart with High Temperature Low Sag conductors. | RES UK & Ireland Limited | Glenluce 132/33kV | Annabaglish | 31/10/2023
SPT-RI-225 | It is proposed to connect Glenmuckloch pump storage 132kV collector substation to New Cumnock 132kV Board C substation via a 22km wood pole overhead line circuit. It is proposed to install a High Temperature Low Sag (HTLS) conductor on the circuit to provide sufficient capacity for the connection of two developments, namely Glenmuckloch pump storage (100MW) and Sanquhar IIA wind farm (99MW). The length of the circuit is approximately 22km and will require a 132kV bay at New Cumnock. The anticipated capability of the circuit will be as in the table below. | Sanquhar II Community Wind Company Limited |  | Sanquhar IIa Community Wind Farm | 30/11/2023
SPT-RI-226 | Installation of a new 275/132kV 360MVA transformer and a new 132kV busbar at Elvanfoot substation, to allow new generators to connect. | Innogy Renewables UK Ltd | Elvanfoot 275/132/33kV | Harryburn Wind Farm | 30/10/2020
SPT-RI-227 | It is proposed to rebuild AK and T Route single circuit Chapelcross to Harker 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 227MVA. The current circuit is a 132kV overhead tower line, with Lynx conductor, with a pre-fault summer continuous rating of 89MVA. This project is in response to the increased level of generation in the area. The 132kV overhead line circuit between Chapelcross and Harker has split ownership, 17.5km from Chapelcross 132kV substation following AK and T route, to tower T137A. This is owned by SPT with the remaining 8.6 km from tower T137A to Harker 132kV substation owned by NGET. Any uprating by SPT will need to be matched by NGET. The project will be to rebuild the SPT-owned 17.5km of AK and T route utilising LARK HTLS conductor on a 132kV wood pole construction. This will provide a pre-fault summer continuous rating of 227MVA. The existing Ak and T route 132kV steel tower circuit will be dismantled. | Community Wind Power Ltd | Faw Side Community Wind Farm | Faw Side Community Wind Farm | 30/11/2024
SPT-RI-229 | A new 400/132kV 240MVA transformer, and associated 400kV and 132kV circuit breaker bays, shall be installed at Moffat 400/132kV substation to increase the available generation capacity at the 132kV substation. | Community Wind Power Ltd | Scoop Hill Wind Farm 132kV Substation | Scoop Hill Wind Farm | 31/12/2023
SPT-RI-230 | It is proposed to reconductor approximately 36km of the 132kV overhead line existing Gretna to Hawick circuit (AL and V Route), between Gretna and the proposed Faw Side Community Wind Farm ‘T’ connection. It is proposed to utilise LARK HTLS conductor. NGET own a section of AL and V Route on this circuit and will have to reinforce to match the SPT proposals. | Community Wind Power Ltd | Faw Side Community Wind Farm | Faw Side Community Wind Farm | 30/11/2024
SPT-RI-232 | Ewe Hill Substation Transformer 132/33kV - Installation of a new 132/33kV 90MVA transformer at Ewe Hill Wind Farm Substation. This will create a new 33kV busbar to allow new generation to connect. (SPT-RI-232). | Loganhead Wind Farm Limited | EWE HILL WF 33/132KV COLLECTOR SUBSTATION | Loganhead Windfarm | 31/10/2023
SPT-RI-233 | Gretna to Jun V 132kV Circuit Reinforcement (AL Route) - Reconductor the AL route single circuit from Gretna to Junction V 132kV overhead line, in order to increase the thermal rating to a minimum summer pre-fault continuous rating of 124MVA. (SPT-RI-233). | Community Wind Power Ltd | Faw Side Community Wind Farm | Faw Side Community Wind Farm | 30/11/2024
|  | Loganhead Wind Farm Limited | EWE HILL WF 33/132KV COLLECTOR SUBSTATION | Loganhead Windfarm | 31/10/2023
SPT-TI-181 | Installation of one 132kV line isolator at Kype Muir Wind Farm Collector Substation. At Coalburn 132kV substation, install a 132kV circuit breaker disconnectors and associated apparatus to create the 132kV bay for the Kype Muir Wind Farm Collector Substation circuit. At Kype Muir Wind farm Collector Substation install a 132kV circuit breaker and associated apparatus to terminate the 132kV cable circuit from Coalburn Substation. | Banks Renewables (Harting Rig Wind Farm) Limited | Harting Rig 132/33kv | Harting Rig Wind Farm | 30/07/2020
|  | Banks Renewables Limited | Coalburn 132/33kV | Kype Muir | 17/09/2018
Stornoway Item 1 | The Relevant Transmission Licensee will construct a 5km single circuit 132kV wood pole overhead line from a fully equipped 132kV feeder bay at Arnish 132kV substation to the windfarm site. The new 132kV line will terminate on the Relevant Transmission’s 132kV line isolator at the User’s 132/33kV windfarm substation. | Lewis Wind Power Ltd | Stornoway 132/33kV Substation | Stornoway Wind Farm
Stranoch Part 1 | 1. Installation of approximately 7.5km of 132kV overhead line from the Stranoch Wind Farm site to the Chirmorie Wind Farm tee point. 2. Installation of a 132kV line isolator at Stranoch Wind Farm substation. | EDF Energy Renewables Limited | Stranoch Wind 132/33KV | Stranoch Wind Farm | 31/10/2017
Strathy Wood Part 1 | 1. Construct a 132kV wood pole trident line over a distance of 5km between Strathy North 132/33kV substation and the new 132/33kV substation at Strathy Wood. The wood pole line will be coupled off one of the incoming 132kV line circuits at Strathy North 132kV substation, and terminated on a new 132kV transformer disconnector switch at Strathy Wood 132/33kV substation. 2. Provision and installation of a 132kV transformer circuit switcher (115) at Strathy Wood 132/33kV substation, installed on the 132kV side of the 132/33kV transformer unit. | E.ON Climate & Renewables UK Developments Limited | Strathy Wood | Strathy Wood | 31/10/2021
Thermal uprate of the Aberthaw – Tremorfa circuit | Thermal uprate of the Aberthaw – Tremorfa circuit | Abernedd Power Company Ltd | Baglan Bay 275kV | Abernedd Power Station | 31/10/2026
Thermal uprate of the Cardiff East – Uskmouth – Whitson circuit | Thermal uprate of the Cardiff East – Uskmouth – Whitson circuit | Abernedd Power Company Ltd | Baglan Bay 275kV | Abernedd Power Station | 31/10/2026
Thermal uprate of the Cardiff East leg of the Pyle – Aberthaw – Cardiff East circuit | Thermal uprate of the Cardiff East leg of the Pyle – Aberthaw – Cardiff East circuit | Abernedd Power Company Ltd | Baglan Bay 275kV | Abernedd Power Station | 31/10/2026
Thermal uprate of the circuits from Whitson – Iron Acton – Melksham | Thermal uprate of the circuits from Whitson – Iron Acton – Melksham | Abernedd Power Company Ltd | Baglan Bay 275kV | Abernedd Power Station | 31/10/2026
Thermal uprate of the Cowley – Walham circuit | Thermal uprate of the Cowley – Walham circuit | Abernedd Power Company Ltd | Baglan Bay 275kV | Abernedd Power Station | 31/10/2026
Thermal uprate of the Imperial Park – Melksham and the Cilfynydd – Whitson – Seabank circuit | Thermal uprate of the Imperial Park – Melksham and the Cilfynydd – Whitson – Seabank circuit (Severn Cable circuits) | Abernedd Power Company Ltd | Baglan Bay 275kV | Abernedd Power Station | 31/10/2026
Thermal uprate of the Uskmouth – Whitson 2 circuit | Thermal uprate of the Uskmouth – Whitson 2 circuit | Abernedd Power Company Ltd | Baglan Bay 275kV | Abernedd Power Station | 31/10/2026
Thermal uprate of Whitson SGT5 | Thermal uprate of Whitson SGT5 | Abernedd Power Company Ltd | Baglan Bay 275kV | Abernedd Power Station | 31/10/2026
Wathegar 2 Item 1 | At the Mybster 132kV extension substation, install 2 x 132kV busbar disconnectors, associated busbar extensions, support structures, protection, control and metering equipment. | Wathegar 2 Limited | Mybster 1 | Wathegar 2 Windfarm | 31/12/2018
Wathegar 2 Item 2 | At Mybster 132/33kV substation, the Relevant Transmission Licensee shall replace the existing 2 x 30 MVA and 1 x 60 MVA 132/33kV transformers with higher rated twin 120MVA 132/33kV transformers within the same substation accommodation. The works will include all associated plinth foundations, transformer protection equipment, and 33kV cabling work associated with the two replacement 120MVA transformers. | Wathegar 2 Limited | Mybster 1 | Wathegar 2 Windfarm | 31/12/2018
Wathegar 2 Item 3 | Install 2 x 132kV transformer circuit breaker bays connected off the Mybster 132kV busbar extension, complete with protection and associated auxiliary equipment. (The incumbent 33kV switchboard and 132kV transformer circuit switchers are adequately rated to meet the 120MVA transformer capacity; hence no further works are required). | Wathegar 2 Limited | Mybster 1 | Wathegar 2 Windfarm | 31/12/2018