## Form
Invitation for Expressions of Interest (EoI), Power Potential Please return completed form by 26th February 2018 by
e-mail
Date of submission: | dd/mm/yyyy
Overview
Please complete fields where applicable. Add additional fields if required.
Company Name
Name of Contact
Job Title
Email Address
Full Mailing Address
Phone Number
Please evidence your capability (experience) of providing similar services as requested in the EoI (e.g. other response programmes, portfolio management, operation)
When can you start providing the service, and at what times of the day?
Dependencies on other flexibility/ancillary services (e.g. STOR, Triad, FFR)
Is there any additional work required to enable your participation (e.g. installing new equipment)?
Please provide a summary of your offer and, if possible, include an indication of cost with assumptions as necessary
Conditions for participation
We are open to all technology types that can meet our requirements. Service providers may represent any existing or new industry sectors and any type of response mechanisms, such as demand reduction, demand offset, generation export, or electrical storage discharge.
Please indicate whether you can meet the high-level service conditions below. If you answer no, please provide further details in the additional notes. |  | Yes/No | Additional notes
1. The DER has to be connected to the network asset being supported. Providers should use the postcode list to check that the resource is in the right geographic location. UK Power Networks will verify that the electrical connection is suitable using the submitted MPANs.
2.Generators and storage looking to export to the network will need to have a long-term parallel connection and be compliant with the requirements of EREC G59/3-2*. Please advise if you require an update to your connection agreement to become compliant.
3. The DER must have system capability to submit 'service availability', defined as the settlement periods for which the service (type of service, reactive or active, and volume, Mvar or MW) is available, 24 hours ahead via a web portal. Include availability price for Reactive Power service in £/Mvar/hr.
4. The DER must have system capability to submit 'service utilisation', defined as the utilisation fee for service, £/Mvarh for reactive service, £/MWh for active service, 24 hours ahead via a web portal.
5. Flexibility providers should be able to deliver the service during any period across the duration of the trial (January – December 2019).
* http://www.dcode.org.uk/assets/images/ENA_EREC_G59_Issue_3_Amendment_2_(2015).pdf
Specific conditions for participation in Reactive Power Service - Only for Non-synchronous DER
6. There are no restrictions on the size of sub-sites of aggregated portfolios, but the total portfolio size needs to be at least 500kvar (flexibility capability and not capacity). Similarly, the minimum size for directly contracted resources should also be at least 500kvar.
7. The non-synchronous DER should be capable of operating in voltage droop control to automatically deliver changes in reactive power in response to system voltage changes.
8. The non-synchronous DER should be able to automatically sweep between voltage droop control and power factor control in an expected time of 10s. In addition, it is expected that any change in voltage target set-point received electronically should be acted on within 2 seconds.
9. The non-synchronous DER should be able to change the voltage set-point of its voltage droop control*, upon UK Power Networks’ request. *Note that the initial droop percentage (i.e. gradient/slope) is expected to be set at 4%.
Specific conditions for participation in Reactive Power Service - Only for Synchronous DER
10. There are no restrictions on the size of sub-sites of aggregated portfolios, but the total portfolio size needs to be at least 500kvar (flexibility capability and not capacity). Similarly, the minimum size for directly contracted resources should also be at least 500kvar.
11. The synchronous DER should be capable of operating to a target voltage set-point to automatically deliver changes in reactive power in response to system voltage changes.
12. The synchronous DER should be able to automatically sweep between target voltage control and power factor control in an expected time of 10s. In addition, it is expected that any change in voltage target set-point received electronically should be acted on within 2 seconds.
13. The synchronous DER should be able to change its target voltage set-point, upon UK Power Networks’ request.
Specific conditions for participation in Active Power Service - Non-synchonous and Synchronous DER
14. There are no restrictions on the size of sub-sites of aggregated portfolios, but the total portfolio size needs to be at least 500kW* (flexibility capability and not capacity). Similarly, the minimum size for directly contracted resources should also be at least 500kW.
15. The DER should be able to deliver and manage, upon UK Power Networks’ request, a net change in the import or a change in the export, as seen by the distribution network.
16. The DER should be able to declare a minimum running time of half an hour (i.e. to declare a capability that can be maintained for half an hour).
* The 500kW threshold is confirmed following the Flexibility Service Design consultation
Site specific details
Please provide as much information as possible
General DER technical characteristics
Network location
Type of customer (e.g. commercial load and technology type)
Import MPAN
Export MPAN
Connection status. If not energised, specify expected connection date.
Provide site P/Q capability characteristics (see section below)
Monitoring and control capability. Can you respond to a dispatch instruction via IP-based communications? Is DER Interface available to RTU - DNP3 over TCP/IP using CAT5e or Fibre?
Provide a control point contact phone, with operational response capability.
Existing metering/monitoring capability and resolution (e.g. minute by minute resolution, MW/Mvar).
Typical generation/demand profile for typical operational scenarios (e.g. winter, summer, triad avoidance, etc.). Provide data/charts if available.
The maximum and minimum time (in minutes) for which you will allow the service to be utilised in a single utilisation. Indicate any other restrictions to utilisation and reasons for those restrictions (e.g. environmental reasons, investors restrictions, etc.)
Reactive Power service: Service-specific DER technical characteristics
Installed reactive power capacity (Mvar)
Lead time from UKPN's instruction reception to DER instruction order
Lead time from DER instruction to voltage set-point change
Lead time to change from PF/Reactive power control to Voltage control
Is the site able to provide reactive power at zero active power output?
Reactive Power service: Service-specific DER technical characteristics - PQ capability chart*
If the PQ capability chart is dependant of voltage, please provide this info for the three following voltage values: 0.94 p.u., 1.0 p.u. and 1.06 p.u.
Lead and lag reactive power (Q) export at maximum active power output (P=100%)
Lead and lag reactive power (Q) export at 95% active power output (P=95%)
Lead and lag reactive power (Q) export at 90% active power output (P=90%)
Lead and lag reactive power (Q) export at 85% active power output (P=85%)
Lead and lag reactive power (Q) export at 80% active power output (P=80%)
Lead and lag reactive power (Q) export at 70% active power output (P=70%)
Lead and lag reactive power (Q) export at 60% active power output (P=60%)
Lead and lag reactive power (Q) export at 50% active power output (P=50%)
Lead and lag reactive power (Q) export at 40% active power output (P=40%)
Lead and lag reactive power (Q) export at 30% active power output (P=30%)
Lead and lag reactive power (Q) export at 20% active power output (P=20%)
Lead and lag reactive power (Q) export at 10% active power output (P=15%)
Lead and lag reactive power (Q) export at 10% active power output (P=10%)
Lead and lag reactive power (Q) export at 5% active power output (P=5%)
Lead and lag reactive power (Q) export at zero active power output (P=0%)
Above capability plotted as a P/Q chart if available (Performance Chart)
* Please refer to the examples below when providing performance charts. PQ capability charts have to be defined for at the point of connection (POC)* for non-synchronous DER and at the generator terminals for synchronous DER.
Synchronous DER | Non-synchronous DER
Reactive Power service: Service-specific DER technical characteristics - Only for Non-synchronous DER
Time taken by automatic voltage droop control to change reactive power from 0 to 90% of maximum export (s) given a sufficiently large change in system voltage
Time taken by automatic voltage droop control to change reactive power from 0 to 90% of maximum import (s) given a sufficiently large change in system voltage
Reactive Power service: Service-specific DER technical characteristics - Only for Synchronous DER (Automatic Voltage Control System)
Excitation system details | Static/brushless exciter? Capable of constant terminal voltage control? Range of voltage set-point?
Generator step-up transformer | Rated power (MVA), Rated voltage (kV), Positive sequence impedance (pu), Tap changer range (+%, -% on MVA), Tap change step size (% on MVA)
Active Power service: Service-specific DER technical characteristics
Installed active power capacity (MW)
Lead time from UKPN's instruction reception to DER instruction order
Lead time from DER instruction to ramp-up/ramp/ramp-down start
Maximum response duration (utilisation time) for MW response (mins)
Recovery time (from end of delivery to when next available to deliver) for Active Power service
Maximum active power (P) export
Maximum active power (P) import
Minimum active power (P) export
Minimum active power (P) import
Ramp Up Rate (MW/s)
Ramp Down Rate (MW/s)
Range of continuous ramping (MW)
Technology-specific DER characteristics
If applicable - Storage Capacity (MWh)
If Wind - Cut In Speed (mph)
If Wind - Saturation Speed (mph)
If Wind - Cutout Speed (mph)
If PV Solar - Reference irradiation (W/m2)
If PV Solar - Reference cell temperature (degC)
If PV Solar - Other cell module data (no. of modules and cells, module open circuit voltage, module short circuit current, module maximum power, ...)